## Introduction
Benchmark Test for a Computer Simulation Person
< Experimental Result of Displacement Ventilation >
Shinsuke Kato | kato@iis.u-tokyo.ac.jp |  | Professor, IIS, University of Tokyo, Japan
Jeong-Hoon Yang | yangjh@iis.u-tokyo.ac.jp |  | Ph.D., IIS, University of Tokyo, Japan
This file is inclued the experimental result of diplacement ventilation for Benchmark Test
This experiment had been carried out by Kato laboratory at University of Tokyo
This file have 11 worksheets
1) Test Condition: |  | Test condition of experiment
2) Supply Opening Detail: |  | Deatail of supply opening air velocity
3) Measurment Position: |  | Measurment position of velocity and temperature in the test room and around thermal manikin
4) Room Velocity: |  | Vertical air velocity and turbulence intensity of the test room
5) Room Temperature: |  | Vertical air temperature of the test room
6) Skin Temperature of Manikin: |  | Skin temperature of thermal manikin in the case of displacement ventilation
7) PIV-Lowerleg: |  | Vector and saclar air velocity around lowerleg of thermal manikin by PIV
8) PIV-Pelvis: |  | Vector and saclar air velocity around pelvis of thermal manikin by PIV
9) PIV-Chest: |  | Vector and saclar air velocity around chest of thermal manikin by PIV
10) PIV-Face: |  | Vector and saclar air velocity around face of thermal manikin by PIV
11) PIV-Head: |  | Vector and saclar air velocity around head of thermal manikin by PIV
This data can be only used for Benchmark Test of Displacement Ventilation

## Test Condition
Experiment Condition of Displacement Ventilation
< Condition of experiment >
1. Test Room Size: | 0.3m X 3.5m X 2.5m
2. Supply Opening Condition: | 1) Velocity: 0.182m/s
2) Size : 0.4m(width) X 0.2m(height)
3) Temperature: 21.8 C
3. Exhaust Opening Condition: | Size : 0.3m(width) X 0.3m(height)
4. Thermal Manikin Condition: | 76W (Area: 1.471m^2, 51.6W/m^2)

## Supply Opening Detail
Supply Opening Detail
(Average of 2times, thermistor anemometer)
0.08m
| about0.07m | 0.16m/s | 0.155m/s | 0.215 | 0.195 | 0.17
|  | 0.115 | 0.18 | 0.16 | 0.19 | 0.18 | 0.2m
|  | 0.17 | 0.19 | 0.205 | 0.22 | 0.21
0.4m
Average of supply air velocity: 0.182 [m/s]

## Measurement Position
Measurement Position of Velocity and Temperature
Measurement Velocity around Thermal Maninkin by PIV

## Room Velocity
Distribution of Air Velosity [m/s]
Air velocity of room was measured by using ultrasonic anemometer.
(Average of 3times, each time was measured 5minitue after stable air velocity)
Height[m] Position | 0.1 | 0.2 | 0.6 | 1 | 1.4 | 1.72
L1 | 0.158 | 0.027 | 0.013 | 0.016 | 0.015 | 0.016
L2 | 0.039 | 0.022 | 0.019 | 0.018 | 0.016 | 0.016
L4 | 0.045 | 0.027 | 0.018 | 0.042 | 0.024 | 0.027
L5 | 0.024 | 0.025 | 0.016 | 0.015 | 0.014 | 0.015
Distribution of Turbulence Intensity [%]
Height[m] Position | 0.1 | 0.2 | 0.6 | 1 | 1.4 | 1.72
L1 | 26 | 46.3 | 57.9 | 53.8 | 55.1 | 54.4
L2 | 46.1 | 41.4 | 43.9 | 51.3 | 49.3 | 54.7
L4 | 35.5 | 49.3 | 53.3 | 44.3 | 51.2 | 56.6
L5 | 48.8 | 37.8 | 53.1 | 55.4 | 58.3 | 57.7

## Room Temperature
Distribution of Air Temperature [°C]
Air temperature of room was measured by using thermocouple of T-type.
(Average of 4times, each time was measured 6hour after stable air temperature)
Height[m] Position | 0.1 | 0.2 | 0.6 | 1 | 1.4 | 1.8 | 2.12
L1 | 22.8 | 25.1 | 25.6 | 26 | 26.1 | 26.3 | 26.4
L2 | 24.7 | 25.2 | 25.8 | 26.1 | 26.2 | 26.3 | 26.4
L4 | 24.7 | 25.1 | 25.7 | 26.4 | 26.4 | 26.4 | 26.8
L5 | 24.9 | 25.1 | 25.7 | 26 | 26.2 | 26.3 | 26.5

## Skin Temperature of Manikin
Skin Temperature of Thermal Manikin [°C]
Thermal Manikin 76W (Area: 1.471m^2, 51.6W/m^2)
(Average of 4times, each time was measured 6hour after stable air temperature)
Region | Temperature[°C]
L. Foot | 30.4687
R. Foot | 30.4669
L. Low Leg | 31.3957
R. Low Leg | 31.4504
L. Thigh | 31.9731
R. Thigh | 32.0231
Pelwis | 32.3306
Head | 32.6508
L. Hand | 32.4664
R. Hand | 32.2913
L. Forearm | 32.6678
R. Forearm | 32.6269
L. Shoulder | 32.6421
R. Shoulder | 32.7764
Chest | 32.6832
Back | 32.7709
All | 32.2037

## PIV-Lowerleg
Velocity around Lowerleg by PIV
Y* [mm] | u [m/s] | v [m/s] | V(=sqrt(u^2+v^2) [m/s]
-136.4479 | 0.001357 | 0.000106 | 0.001361
-133.6052 | 0.001383 | 9.7e-05 | 0.001387
-130.7626 | 0.00143 | 1.3e-05 | 0.00143
-127.9199 | 0.001498 | -6e-05 | 0.001499
-125.0772 | 0.001574 | -0.000155 | 0.001582
-122.2346 | 0.001705 | -0.000236 | 0.001721
-119.3919 | 0.001812 | -0.000346 | 0.001844
-116.5492 | 0.001908 | -0.000417 | 0.001953
-113.7066 | 0.001944 | -0.000501 | 0.002007
-110.8639 | 0.001994 | -0.000622 | 0.002088
-108.0212 | 0.002046 | -0.000804 | 0.002199
-105.1786 | 0.002107 | -0.000956 | 0.002313
-102.3359 | 0.002194 | -0.001082 | 0.002447
-99.4932 | 0.002305 | -0.001218 | 0.002607
-96.6506 | 0.002325 | -0.001341 | 0.002684
-93.8079 | 0.002377 | -0.001431 | 0.002775 | Measurement Position
-90.9652 | 0.002529 | -0.001488 | 0.002934
-88.1226 | 0.002826 | -0.001546 | 0.003221
-85.2799 | 0.003122 | -0.001589 | 0.003503
-82.4372 | 0.003277 | -0.001617 | 0.003654
-79.5946 | 0.003464 | -0.001645 | 0.003834
-76.7519 | 0.003653 | -0.001695 | 0.004027
-73.9092 | 0.00387 | -0.00176 | 0.004252
-71.0666 | 0.004031 | -0.001786 | 0.00441
-68.2239 | 0.004179 | -0.001735 | 0.004525
-65.3812 | 0.004355 | -0.001559 | 0.004625
-62.5386 | 0.004529 | -0.001285 | 0.004708
-59.6959 | 0.004705 | -0.000819 | 0.004776
-56.8533 | 0.004866 | -8.3e-05 | 0.004866
-54.0106 | 0.00502 | 0.000982 | 0.005116
-51.1679 | 0.005169 | 0.002242 | 0.005634
-48.3253 | 0.00524 | 0.003813 | 0.00648
-45.4826 | 0.005265 | 0.005659 | 0.00773
-42.6399 | 0.005207 | 0.007873 | 0.009439
-39.7973 | 0.005172 | 0.010389 | 0.011605 | Distribution of Vector Velocity
-36.955 | 0.005095 | 0.013191 | 0.014141
-34.112 | 0.005001 | 0.016419 | 0.017163
-31.269 | 0.004833 | 0.020082 | 0.020655
-28.427 | 0.004703 | 0.024321 | 0.024772
-25.584 | 0.004581 | 0.029096 | 0.029455
-22.741 | 0.004415 | 0.034348 | 0.03463
-19.899 | 0.004049 | 0.04033 | 0.040532
-17.056 | 0.003525 | 0.047167 | 0.047299
-14.213 | 0.002811 | 0.055477 | 0.055548
-11.371 | 0.002058 | 0.065797 | 0.065829
-8.528 | 0.001284 | 0.078204 | 0.078215
-5.685 | 0.000565 | 0.090837 | 0.090839
-2.843 | 0.000101 | 0.099171 | 0.099171
0 | 9.7e-05 | 0.068918 | 0.068918
Distribution of Scalar Velocity
70mm
mm
mm
mm
mm
Y:u
Z:v
X

## PIV-Pelvis
Velocity around Pelvis by PIV
Y* [mm] | u [m/s] | v [m/s] | V(=sqrt(u^2+v^2) [m/s]
-182.8049 | 0.004979 | 0.002078 | 0.005396
-179.5978 | 0.005053 | 0.002097 | 0.005471
-176.3907 | 0.005184 | 0.002174 | 0.005621
-173.1836 | 0.005324 | 0.00232 | 0.005807
-169.9765 | 0.005505 | 0.002574 | 0.006077
-166.7694 | 0.005653 | 0.002862 | 0.006336
-163.5623 | 0.005753 | 0.003151 | 0.00656
-160.3552 | 0.005798 | 0.003477 | 0.00676
-157.1481 | 0.005899 | 0.00383 | 0.007033
-153.941 | 0.005929 | 0.00421 | 0.007272
-150.7339 | 0.00599 | 0.004512 | 0.007499
-147.5268 | 0.005977 | 0.004889 | 0.007722
-144.3197 | 0.005987 | 0.005377 | 0.008047 | Measurement Position
-141.1126 | 0.005912 | 0.006127 | 0.008514
-137.9055 | 0.005941 | 0.007109 | 0.009265
-134.6984 | 0.006034 | 0.008211 | 0.01019
-131.4913 | 0.006189 | 0.009427 | 0.011277
-128.2842 | 0.006317 | 0.010604 | 0.012343
-125.0771 | 0.006443 | 0.012018 | 0.013636
-121.87 | 0.006533 | 0.01357 | 0.015061
-118.6629 | 0.006597 | 0.015436 | 0.016786
-115.4558 | 0.00661 | 0.017676 | 0.018872
-112.2487 | 0.006657 | 0.02045 | 0.021506
-109.0416 | 0.006794 | 0.023963 | 0.024908
-105.8345 | 0.006949 | 0.028073 | 0.028921
-102.6274 | 0.007024 | 0.032692 | 0.033438
-99.4203 | 0.006855 | 0.037188 | 0.037815
-96.2132 | 0.006501 | 0.04158 | 0.042085
-93.0061 | 0.005888 | 0.045792 | 0.046169
-89.799 | 0.005272 | 0.05083 | 0.051103
-86.5919 | 0.004431 | 0.056229 | 0.056404
-83.385 | 0.003709 | 0.06221 | 0.062321
-80.178 | 0.002736 | 0.06786 | 0.067915 | Distribution of Vector Velocity
-76.971 | 0.001789 | 0.073702 | 0.073724
-73.764 | 0.000761 | 0.079237 | 0.07924
-70.556 | 8.8e-05 | 0.084542 | 0.084542
-67.349 | -0.000338 | 0.089682 | 0.089682
-64.142 | -0.000604 | 0.09517 | 0.095172
-60.935 | -0.000691 | 0.10142 | 0.10143
-57.728 | -0.00061 | 0.108 | 0.108
-54.521 | -0.000155 | 0.11456 | 0.11456
-51.314 | 0.000379 | 0.12073 | 0.12073
-48.107 | 0.000869 | 0.12622 | 0.12623
-44.9 | 0.001054 | 0.13073 | 0.13073
-41.693 | 0.001194 | 0.13406 | 0.13407
-38.485 | 0.001586 | 0.1368 | 0.13681
-35.278 | 0.002324 | 0.1391 | 0.13912
-32.071 | 0.003294 | 0.14115 | 0.14119
-28.864 | 0.004463 | 0.14303 | 0.14309
-25.657 | 0.00579 | 0.14504 | 0.14516
-22.45 | 0.007622 | 0.14737 | 0.14756 | Distribution of Scalar Velocity
-19.243 | 0.009988 | 0.15003 | 0.15036
-16.036 | 0.013 | 0.15326 | 0.15381
-12.829 | 0.015925 | 0.15665 | 0.15746
-9.621 | 0.018246 | 0.15852 | 0.15957
-6.414 | 0.019003 | 0.15425 | 0.15541
-3.207 | 0.015345 | 0.12707 | 0.128
0 | 0.009061 | 0.08421 | 0.084696
79mm
mm
mm
mm
mm
Y:u
Z:v
X

## PIV-Chest
Velocity around Chest by PIV
Measurement Position
Distribution of Vector Velocity
Distribution of Scalar Velocity
mm
mm
mm
mm
Y:u
Z:v
X

## PIV-Face
Velocity around Face by PIV
Y* [mm] | u [m/s] | v [m/s] | V(=sqrt(u^2+v^2) [m/s]
-167.472 | 0.002672 | 0.002881 | 0.003929
-164.4271 | 0.002611 | 0.003058 | 0.004021
-161.3821 | 0.002502 | 0.003385 | 0.004209
-158.3372 | 0.00245 | 0.003712 | 0.004448
-155.2922 | 0.002377 | 0.004035 | 0.004683
-152.2473 | 0.002311 | 0.004213 | 0.004805
-149.2023 | 0.002242 | 0.004426 | 0.004961
-146.1574 | 0.002276 | 0.005042 | 0.005532
-143.1124 | 0.002266 | 0.005992 | 0.006406
-140.0675 | 0.002282 | 0.006983 | 0.007346
-137.0225 | 0.002324 | 0.007779 | 0.008118
-133.9776 | 0.002465 | 0.008644 | 0.008988
-130.9326 | 0.002675 | 0.009641 | 0.010005
-127.8877 | 0.002804 | 0.010834 | 0.011191
-124.8427 | 0.002911 | 0.012049 | 0.012396 | Measurement Position
-121.7978 | 0.003001 | 0.013222 | 0.013558
-118.7528 | 0.003115 | 0.014289 | 0.014624
-115.7078 | 0.003345 | 0.015552 | 0.015907
-112.6629 | 0.003648 | 0.017086 | 0.017471
-109.6179 | 0.003974 | 0.018973 | 0.019384
-106.573 | 0.004225 | 0.021026 | 0.021446
-103.528 | 0.004503 | 0.022979 | 0.023416
-100.4831 | 0.004831 | 0.025021 | 0.025483
-97.4381 | 0.005258 | 0.027236 | 0.027739
-94.3932 | 0.005527 | 0.029801 | 0.030309
-91.3482 | 0.005808 | 0.032168 | 0.032688
-88.3033 | 0.006145 | 0.034419 | 0.034963
-85.2583 | 0.006557 | 0.03678 | 0.03736
-82.2134 | 0.00677 | 0.039349 | 0.039927
-79.1684 | 0.006762 | 0.041876 | 0.042418
-76.1235 | 0.006655 | 0.044231 | 0.044729
-73.0785 | 0.006463 | 0.046525 | 0.046972
-70.0336 | 0.00641 | 0.04888 | 0.049298
-66.989 | 0.006567 | 0.051136 | 0.051556 | Distribution of Vector Velocity
-63.944 | 0.006932 | 0.053563 | 0.054009
-60.899 | 0.007452 | 0.056037 | 0.056531
-57.854 | 0.007746 | 0.058632 | 0.059142
-54.809 | 0.008252 | 0.060703 | 0.061261
-51.764 | 0.008748 | 0.062832 | 0.063438
-48.719 | 0.009843 | 0.064797 | 0.06554
-45.674 | 0.011277 | 0.067059 | 0.068001
-42.629 | 0.013267 | 0.069351 | 0.070608
-39.584 | 0.015384 | 0.071948 | 0.073574
-36.539 | 0.018096 | 0.07447 | 0.076638
-33.494 | 0.021512 | 0.076196 | 0.079175
-30.449 | 0.026202 | 0.077502 | 0.081811
-27.404 | 0.032389 | 0.078156 | 0.084601
-24.359 | 0.041024 | 0.078463 | 0.088541
-21.314 | 0.052988 | 0.077411 | 0.09381
-18.269 | 0.070457 | 0.074762 | 0.10273
-15.224 | 0.095319 | 0.068897 | 0.11761
-12.179 | 0.12308 | 0.058092 | 0.13611 | Distribution of Scalar Velocity
-9.135 | 0.12259 | 0.045562 | 0.13079
-6.09 | 0.081309 | 0.026325 | 0.085465
-3.045 | 0.029266 | 0.011103 | 0.031301
0 | 0.001137 | 4.7e-05 | 0.001138
38.6mm
mm
mm
mm
mm
Y:u
Z:v
X

## PIV-Head
Velocity around Head by PIV
Z* [mm] | u [m/s] | v [m/s] | V(=sqrt(u^2+v^2) [m/s]
1.9311 | 0.005091 | 0.004082 | 0.006525
4.8278 | 0.005766 | 0.005728 | 0.008127
7.7244 | 0.006815 | 0.009403 | 0.011613
10.6211 | 0.007436 | 0.014134 | 0.015971
13.5177 | 0.007549 | 0.01971 | 0.021106
16.4144 | 0.007273 | 0.025988 | 0.026987
19.311 | 0.006426 | 0.032655 | 0.033281
22.2077 | 0.005135 | 0.039715 | 0.040046
25.1043 | 0.003713 | 0.046909 | 0.047056
28.001 | 0.002364 | 0.054146 | 0.054198
30.8977 | 0.001044 | 0.061271 | 0.06128
33.7943 | -0.000408 | 0.06828 | 0.068281
36.691 | -0.001713 | 0.075186 | 0.075205
39.5876 | -0.002787 | 0.082003 | 0.082051
42.4843 | -0.003528 | 0.088653 | 0.088724
45.3809 | -0.004059 | 0.095059 | 0.095146
48.2776 | -0.004607 | 0.10117 | 0.10128 | Measurement Position
51.1743 | -0.005244 | 0.10701 | 0.10713
54.0709 | -0.005951 | 0.1126 | 0.11276
56.9676 | -0.006645 | 0.11795 | 0.11814
59.8642 | -0.007355 | 0.12306 | 0.12328
62.7609 | -0.008159 | 0.12785 | 0.12811
65.6575 | -0.00894 | 0.1324 | 0.1327
68.5542 | -0.009649 | 0.13664 | 0.13698
71.4508 | -0.010212 | 0.14061 | 0.14098
74.3475 | -0.010722 | 0.14428 | 0.14468
77.2442 | -0.011084 | 0.14774 | 0.14816
80.1408 | -0.011369 | 0.1511 | 0.15153
83.0375 | -0.011629 | 0.15439 | 0.15483
85.9341 | -0.011878 | 0.15752 | 0.15797
88.8308 | -0.012191 | 0.16071 | 0.16117
91.7274 | -0.012438 | 0.16378 | 0.16426
94.6241 | -0.012591 | 0.16689 | 0.16737
97.5207 | -0.012583 | 0.1697 | 0.17017
100.417 | -0.012473 | 0.17247 | 0.17292
103.314 | -0.012347 | 0.17503 | 0.17547
106.211 | -0.012137 | 0.17751 | 0.17792 | Distribution of Vector Velocity
109.107 | -0.011911 | 0.1799 | 0.18029
112.004 | -0.011708 | 0.18228 | 0.18266
114.901 | -0.011517 | 0.18463 | 0.18499
117.797 | -0.011339 | 0.18685 | 0.18719
120.694 | -0.011235 | 0.18892 | 0.18926
123.591 | -0.011408 | 0.19092 | 0.19126
126.487 | -0.011785 | 0.19273 | 0.19309
129.384 | -0.012209 | 0.19428 | 0.19466
132.281 | -0.012351 | 0.19562 | 0.19601
135.177 | -0.012178 | 0.19697 | 0.19735
138.074 | -0.011925 | 0.19788 | 0.19823
140.971 | -0.011795 | 0.19835 | 0.1987
Distribution of Scalar Velocity
Y:u
Z:v
X
11.6mm
mm
mm
mm
mm