## Information
Benchmark Tests for Computer Simulated Persons
Personal Ventilation
All measurements are performed with the detailed manikin shown above.
The spreadsheet contains 8 worksheets
1) Test Condition: | Test condition of experiment
2) Measurement Position: | Measurement position of concentration in the test room
3) Tu Profile for PV jet: | Turbulent intensity profile at the PV nozzle exit
4) Vertical Profiles (2.4 l/s): | Vertical concentration profiles data 1 and 2.5 cm from the manikins nose
5) Vertical Profile Plot (2.4 l/s): | Vertical concentration profiles 1 and 2.5 cm from the manikins nose
6) Vertical Profiles (4.8 l/s): | Vertical concentration profiles data 1 and 2.5 cm from the manikins nose
7) Vertical Profile Plot (2.4 l/s): | Vertical concentration profiles 1 and 2.5 cm from the manikins nose
8) Experimental Error: | Expermintal error in measurments
The data can be used and distributed freely.
For further information please contact
H.E. Khalifa | hekhalif@syr.edu | Syracuse University
J. Russo | jsrusso@syr.edu | Syracuse University

## Experimental Conditions
Test Conditions of Experiment
< Condition of experiment >
| 1. Test Room Size: | 2m X 2.6m X 2.5m
| 2. Floor Diffuser Conditions: | 1) Flow rate: 35 cfm
2) Size : 0.23m x 0.24m with a four way directional grill panel insert
3) Temperature: 20.5 °C
| 3. PV Nozzle Conditions: | 1) Flow rate: 5 cfm
2) Size : 0.05m diameter circular opening
3) Temperature:23.5 °C
4) Turbulent Intensity: 1.7%
| 4. Exhaust Opening Condition: | Size : 0.58m X 1.17m
| 5. Thermal Manikin Condition: | 32°C (Area: 1.5 m2, not including portion of manikin in contact with seat bottom)

## Meausement Positons
Measurement Positions
Measurements were taken 1 cm and 2.5 cm from the manikins nose along the manikin bisecting plane

## Tu Profile
Turbulent Intensity profile at the PV nozzle exit

## Vertical Conc. data (2.4ls)
Vertical Concentration Data (2.4 l/s)
1 cm from nose |  |  | 2.5 cm from nose
Average Conc. (ppm) | AQI | y/R | Average Conc. (ppm) | AQI | y/R
43.5 | -0.11556 | -3.5 | 43.845 | -0.11391 | -3.5
43.84 | -0.12436 | -3.3031 | 43.94 | -0.11634 | -3.3031
44.275 | -0.13563 | -3.1063 | 43.445 | -0.10364 | -3.1063
24.985 | 0.36405 | -0.5 | 29.1 | 0.26443 | -0.5
21.5 | 0.45433 | -0.40157 | 27.115 | 0.31537 | -0.40157
22.395 | 0.43114 | -0.30315 | 29.295 | 0.25943 | -0.30315
23.36 | 0.40615 | -0.20472 | 28.045 | 0.2915 | -0.20472
23.58 | 0.40045 | -0.1063 | 23.025 | 0.42031 | -0.1063
27.78 | 0.29165 | 2.5 | 30.315 | 0.23326 | 2.5
28.01 | 0.28569 | 2.5984 | 30.76 | 0.22184 | 2.5984
27.585 | 0.2967 | 2.6969 | 33.3 | 0.15667 | 2.6969
27.35 | 0.30279 | 2.7953 | 32.685 | 0.17245 | 2.7953
29.425 | 0.24904 | 2.8937 | 31.9 | 0.19259 | 2.8937
40.185 | -0.029684 | 5.5 | 39.61 | -0.0052406 | 5.5
40.19 | -0.029814 | 5.6969 | 39.695 | -0.0074216 | 5.6969
39.05 | -0.00028332 | 5.8937 | 39.32 | 0.0022004 | 5.8937
42.73 | -0.095609 | -4 | 43.84 | -0.11378 | -4
43.505 | -0.11568 | -3.8031 | 43.9 | -0.11532 | -3.8031
43.8 | -0.12333 | -3.6063 | 43.55 | -0.10634 | -3.6063
30.695 | 0.21614 | -1 | 33.895 | 0.1414 | -1
29.81 | 0.23907 | -0.90157 | 34.51 | 0.12562 | -0.90157
30.03 | 0.23337 | -0.80315 | 34.345 | 0.12985 | -0.80315
27.52 | 0.29839 | -0.70472 | 32.435 | 0.17886 | -0.70472
28.735 | 0.26691 | -0.6063 | 29.06 | 0.26546 | -0.6063
24.805 | 0.36872 | 2 | 26.66 | 0.32704 | 2
26.015 | 0.33737 | 2.0984 | 27.85 | 0.29651 | 2.0984
26.665 | 0.32054 | 2.1969 | 26.7 | 0.32601 | 2.1969
26.44 | 0.32636 | 2.2953 | 27.785 | 0.29817 | 2.2953
28.74 | 0.26678 | 2.3937 | 28.63 | 0.27649 | 2.3937
39.7 | -0.017121 | 5 | 37.24 | 0.055571 | 5
37.47 | 0.040645 | 5.1969 | 38.785 | 0.015928 | 5.1969
36.695 | 0.06072 | 5.3937 | 40.505 | -0.028205 | 5.3937
43.19 | -0.10753 | -4.5 | 43.87 | -0.11455 | -4.5
43.905 | -0.12605 | -4.3031 | 43.815 | -0.11314 | -4.3031
44.09 | -0.13084 | -4.1063 | 43.615 | -0.108 | -4.1063
35.635 | 0.088178 | -1.5 | 40.98 | -0.040393 | -1.5
34.44 | 0.11913 | -1.4016 | 36 | 0.087388 | -1.4016
32.605 | 0.16667 | -1.3031 | 36.05 | 0.086105 | -1.3031
31.85 | 0.18622 | -1.2047 | 36.79 | 0.067117 | -1.2047
33.115 | 0.15346 | -1.1063 | 37.15 | 0.05788 | -1.1063
22.925 | 0.41742 | 1.5 | 22.955 | 0.42211 | 1.5
23.015 | 0.41508 | 1.5984 | 23.505 | 0.40799 | 1.5984
23.62 | 0.39941 | 1.6969 | 25.025 | 0.36899 | 1.6969
23.135 | 0.41198 | 1.7953 | 25.89 | 0.3468 | 1.7953
24.65 | 0.37273 | 1.8937 | 25.185 | 0.36489 | 1.8937
35.425 | 0.093618 | 4.5 | 39.62 | -0.0054972 | 4.5
37.675 | 0.035334 | 4.6969 | 39.385 | 0.00053261 | 4.6969
36.355 | 0.069527 | 4.8937 | 36.73 | 0.068657 | 4.8937
44.428 | -0.13959 | -5 | 43.905 | -0.11545 | -5
44.315 | -0.13667 | -4.8031 | 43.86 | -0.11429 | -4.8031
43.915 | -0.12631 | -4.6063 | 43.545 | -0.10621 | -4.6063
42.955 | -0.10144 | -2 | 42.06 | -0.068105 | -2
41.275 | -0.057919 | -1.9016 | 42.155 | -0.070542 | -1.9016
38.195 | 0.021864 | -1.8031 | 40.435 | -0.026409 | -1.8031
37.725 | 0.034039 | -1.7047 | 41.44 | -0.052196 | -1.7047
37.655 | 0.035852 | -1.6063 | 41.305 | -0.048732 | -1.6063
20.455 | 0.4814 | 1 | 21.92 | 0.44866 | 1
21.515 | 0.45394 | 1.0984 | 21.615 | 0.45649 | 1.0984
20.58 | 0.47816 | 1.1969 | 19.89 | 0.50075 | 1.1969
21.765 | 0.44746 | 1.2953 | 22.42 | 0.43583 | 1.2953
23.425 | 0.40446 | 1.3937 | 23.13 | 0.41762 | 1.3937
32.885 | 0.15941 | 4 | 36.125 | 0.08418 | 4
37.345 | 0.043883 | 4.1969 | 37.56 | 0.04736 | 4.1969
36.05 | 0.077428 | 4.3937 | 38.34 | 0.027346 | 4.3937
44.29 | -0.13602 | -5.5 | 43.915 | -0.1157 | -5.5
44.39 | -0.13861 | -5.3031 | 43.93 | -0.11609 | -5.3031
44.495 | -0.14133 | -5.1063 | 43.625 | -0.10826 | -5.1063
43.445 | -0.11413 | -2.5 | 43.08 | -0.094277 | -2.5
42.89 | -0.099754 | -2.4016 | 43.63 | -0.10839 | -2.4016
42.215 | -0.082269 | -2.3031 | 43.045 | -0.093378 | -2.3031
42.125 | -0.079938 | -2.2047 | 43.325 | -0.10056 | -2.2047
41.945 | -0.075275 | -2.1063 | 41.49 | -0.053479 | -2.1063
21.45 | 0.45562 | 0.5 | 20.015 | 0.49754 | 0.5
22.23 | 0.43542 | 0.59843 | 22.415 | 0.43596 | 0.59843
20.24 | 0.48697 | 0.69685 | 20.5 | 0.4851 | 0.69685
20.305 | 0.48528 | 0.79528 | 19.595 | 0.50832 | 0.79528
20.54 | 0.4792 | 0.8937 | 23.115 | 0.418 | 0.8937
32.125 | 0.1791 | 3.5 | 34.965 | 0.11394 | 3.5
35.035 | 0.10372 | 3.6969 | 35.475 | 0.10086 | 3.6969
35.015 | 0.10424 | 3.8937 | 36.6 | 0.071992 | 3.8937
44.405 | -0.139 | -6 | 44.03 | -0.11865 | -6
44.37 | -0.13809 | -5.8031 | 43.995 | -0.11775 | -5.8031
44.425 | -0.13952 | -5.6063 | 43.535 | -0.10595 | -5.6063
44.075 | -0.13045 | -3 | 43.325 | -0.10056 | -3
43.665 | -0.11983 | -2.9016 | 43.655 | -0.10903 | -2.9016
43.7 | -0.12074 | -2.8031 | 43.505 | -0.10518 | -2.8031
43.68 | -0.12022 | -2.7047 | 43.57 | -0.10685 | -2.7047
42.6 | -0.092242 | -2.6063 | 43.85 | -0.11403 | -2.6063
20.845 | 0.4713 | 0 | 24.405 | 0.3849 | 0
21.44 | 0.45588 | 0.098425 | 23.355 | 0.41184 | 0.098425
22.235 | 0.43529 | 0.19685 | 23.785 | 0.40081 | 0.19685
20.815 | 0.47207 | 0.29528 | 21.275 | 0.46521 | 0.29528
21.99 | 0.44164 | 0.3937 | 18.305 | 0.54142 | 0.3937
28.57 | 0.27119 | 3 | 33.075 | 0.16244 | 3
31.755 | 0.18868 | 3.1969 | 34.945 | 0.11446 | 3.1969
33.525 | 0.14284 | 3.3937 | 33.97 | 0.13947 | 3.3937

## Conc. plot (2.4 ls)
Concentration Plot 1 and 2.5 cm from the nose (2.4 l/s)

## Vertical Conc. data (4.7ls)
Vertical Concentration Data (4.7 l/s)
1 cm from nose
Average Conc. (ppm) | AQI | y/R
40.85 | -0.14871 | -3.5
40.46 | -0.13759 | -3.3031
40.86 | -0.14899 | -3.1063
19.93 | 0.44773 | -0.5
18.69 | 0.48309 | -0.40157
17.6 | 0.51416 | -0.30315
16.545 | 0.54424 | -0.20472
16.675 | 0.54053 | -0.1063
26.72 | 0.25415 | 2.5
27.015 | 0.24573 | 2.5984
29.64 | 0.17089 | 2.6969
29.035 | 0.18814 | 2.7953
30.84 | 0.13668 | 2.8937
40.55 | -0.14016 | 5.5
37.965 | -0.066456 | 5.6969
40.99 | -0.1527 | 5.8937
40.175 | -0.12946 | -4
39.735 | -0.11692 | -3.8031
39.99 | -0.12419 | -3.6063
24.325 | 0.32243 | -1
23.69 | 0.34053 | -0.90157
21.33 | 0.40782 | -0.80315
20.86 | 0.42122 | -0.70472
19.845 | 0.45016 | -0.6063
23.21 | 0.35422 | 2
24.14 | 0.3277 | 2.0984
25.9 | 0.27752 | 2.1969
26.445 | 0.26199 | 2.2953
25.74 | 0.28209 | 2.3937
40.945 | -0.15142 | 5
41.2 | -0.15869 | 5.1969
41.08 | -0.15527 | 5.3937
39.985 | -0.12405 | -4.5
39.515 | -0.11065 | -4.3031
39.44 | -0.10851 | -4.1063
31.42 | 0.12015 | -1.5
29.05 | 0.18772 | -1.4016
27.58 | 0.22963 | -1.3031
29.035 | 0.18814 | -1.2047
25.55 | 0.2875 | -1.1063
20.095 | 0.44303 | 1.5
20.89 | 0.42036 | 1.5984
21.195 | 0.41167 | 1.6969
22.105 | 0.38572 | 1.7953
22.38 | 0.37788 | 1.8937
37 | -0.038944 | 4.5
38.565 | -0.083563 | 4.6969
39.735 | -0.11692 | 4.8937
40.08 | -0.12676 | -5
38.96 | -0.094824 | -4.8031
39.53 | -0.11108 | -4.6063
38.105 | -0.070448 | -2
36.44 | -0.022978 | -1.9016
35.665 | -0.00088205 | -1.8031
33.1 | 0.072248 | -1.7047
32.46 | 0.090494 | -1.6063
16.385 | 0.5488 | 1
16.91 | 0.53383 | 1.0984
17.315 | 0.52229 | 1.1969
19.04 | 0.47311 | 1.2953
19.01 | 0.47396 | 1.3937
37.395 | -0.050205 | 4
38.27 | -0.075152 | 4.1969
38.44 | -0.079999 | 4.3937
38.765 | -0.089265 | -5.5
39.02 | -0.096535 | -5.3031
39.955 | -0.12319 | -5.1063
41.1 | -0.15584 | -2.5
39.17 | -0.10081 | -2.4016
39.43 | -0.10822 | -2.3031
38.225 | -0.073869 | -2.2047
36.715 | -0.030818 | -2.1063
14.16 | 0.61224 | 0.5
13.93 | 0.6188 | 0.59843
14.965 | 0.58929 | 0.69685
16.025 | 0.55907 | 0.79528
15.7 | 0.56833 | 0.8937
34.99 | 0.018363 | 3.5
34.475 | 0.033046 | 3.6969
36.365 | -0.020839 | 3.8937
37.74 | -0.060042 | -6
35.645 | -0.00031183 | -5.8031
37.12 | -0.042365 | -5.6063
41.075 | -0.15512 | -3
40.645 | -0.14286 | -2.9016
42 | -0.1815 | -2.8031
41.025 | -0.1537 | -2.7047
40.285 | -0.1326 | -2.6063
15.31 | 0.57945 | 0
15.52 | 0.57346 | 0.098425
14.83 | 0.59314 | 0.19685
14.69 | 0.59713 | 0.29528
15.29 | 0.58002 | 0.3937
30.66 | 0.14181 | 3
34.285 | 0.038463 | 3.1969
34.75 | 0.025205 | 3.3937

## Conc. plot (4.7 ls)
Concentration plot 1 cm from the nose (4.7 l/s)

## Error Analysis
Error Analysis (2.4 l/s 1cm from the nose)