## Information
Benchmark Tests for Computer Simulated Persons
Manikin Heat Loss
C
All measurements are performed with the detailed manikin TM4 Comfortina of Nille type shown above to the right.
The manikin is run in constant surface temperature mode at 34ºC without clothing.
The spreadsheet contains 6 worksheets
Heat loss va 0.27 ta 20 | Mean Inlet velocity | 0.2672 | m/s | Mean Air temp. | 20.4219 | ºC | Total Manikin Heat Loss | 122.3429 | W/m2
Heat loss va 0.27 ta 20 | Mean Inlet velocity | 0.2672 | m/s | Mean Air temp. | 20.4223 | ºC | Total Manikin Heat Loss | 122.5571 | W/m2
Heat loss va 0.27 ta 20 | Mean Inlet velocity | 0.2672 | m/s | Mean Air temp. | 20.3956 | ºC | Total Manikin Heat Loss | 123.3 | W/m2
Heat loss va 0.27 ta 20 | Mean Inlet velocity | 0.2672 | m/s | Mean Air temp. | 20.337 | ºC | Total Manikin Heat Loss | 123.8286 | W/m2
Heat loss va 0.27 ta 20 | Mean Inlet velocity | 0.2672 | m/s | Mean Air temp. | 20.341 | ºC | Total Manikin Heat Loss | 124.0048 | W/m2
Heat loss va 0.27 ta 20 | Mean Inlet velocity | 0.2672 | m/s | Mean Air temp. | 20.3034 | ºC | Total Manikin Heat Loss | 124.0762 | W/m2
The data can be used freely for CFD benchmark testing as long as they are referred to in a proper way:
Benchmark Tests for a Computer Simulated Person - Manikin Heat Loss for Thermal Comfort Evaluation
Håkan O. Nilsson, Henrik Brohus, Mikael K. Jensen and Peter V. Nielsen.
A cooperation between Aalborg University, Denmark and Gävle University, Sweden
February 2007, http://www.cfd-benchmarks.com/
For further information please contact
Håkan O. Nilsson | hnn@hig.se | University of Gävle, Department of Technology and Built Environment, Laboratory of Ventilation and Air Quality
Henrik Brohus | hb@civil.auc.dk | Aalborg University and International Centre for Indoor Environment and Energy
Peter V. Nielsen | pvn@civil.auc.dk | Aalborg University and International Centre for Indoor Environment and Energy

## HL1@va0.27ta20
Manikin heat loss in windtunnel
| Nom. Inlet velocity |  | 0.2 | m/s | Nom. Air temperature |  | 20 | ºC
| Mean Inlet velocity |  | 0.2672 | m/s | Mean Air temp. |  | 20.4219 | ºC
[10 empty] | 1 |  | 2 | [15 empty] | 2
| Std. dev. Inlet vel. |  | 0.0172 | m/s | Std. dev. Air temp. |  | 0.054671 | ºC
1
| Mean Inlet Turb. intens. |  | 6.2906 | % | Mean Wall temp. |  | 21.1298 | ºC
| Relative Humidity |  | 35 | % | Air Pressure |  | 1027.15 | mbar | 4 |  |  | 3 | [12 empty] | 6 | [6 empty] | 5
| Thermal manikin: |  | Comfortina, No clothing, Software version 3.0.30. | [6 empty] | 6 | [17 empty] | 3
| Body Segments |  | Heat loss (W/m2) | [30 empty] | H L (W/m2) | Zones | No
|  | Q [W/m2] | STD [W/m2] | Min | Max | [7 empty] | 8 |  |  |  | 10 | [7 empty] | 10 | [6 empty] | 11 |  | 122.3429 | Total | 18
1 | L. Foot | 153.3714 | 2.1818 | 148.3 | 156.3 | [28 empty] | 71.6381 | Scalp | 9 | 1
2 | R. Foot | 159.6714 | 1.9053 | 155.9 | 162.4 |  |  |  |  | 17 | [23 empty] | 119.481 | Face | 8 | 2
3 | L. Low leg | 142.7143 | 0.5434 | 141.6 | 143.9 | [28 empty] | 117.0429 | Chest | 16 | 3
4 | R. Low leg | 144.6095 | 0.9359 | 142.9 | 146.2 | [5 empty] | 18 |  |  |  |  | 12 | [9 empty] | 12 |  | 18 |  | 11 |  |  |  | 110.6857 | Up. back | 17 | 4
5 | L. Thigh | 100.0286 | 0.42443 | 99.2 | 101.1 | [28 empty] | 122.0238 | L U arm | 14 | 5
6 | R. Thigh | 104.481 | 0.40077 | 103.1 | 105 | [28 empty] | 129.6095 | R U arm | 15 | 6
7 | Pelvis | 112.9095 | 0.5735 | 111.9 | 114.1 | [28 empty] | 153.0048 | L L arm | 12 | 7
8 | Head | 119.481 | 0.52404 | 118.4 | 120.3 | [28 empty] | 130.9429 | R L arm | 13 | 8
9 | Top of head | 71.6381 | 0.44326 | 70.8 | 72.7 | [14 empty] | 14 | [5 empty] | 14 |  |  |  | 13 |  |  |  | 163.0333 | L hand | 10 | 9
10 | L. Hand | 163.0333 | 0.65904 | 162 | 164.1 | [28 empty] | 185.2 | R hand | 11 | 10
11 | R. Hand | 185.2 | 1.283 | 182.3 | 186.6 | [28 empty] | 100.0286 | L thigh | 5 | 11
12 | L. Forearm | 153.0048 | 1.1205 | 150.8 | 154.6 |  |  |  | y | [19 empty] | y |  |  |  |  | 104.481 | R thigh | 6 | 12
13 | R. Forearm | 130.9429 | 1.1325 | 128.8 | 133 | [14 empty] | 16 | [5 empty] | 16 |  |  |  | 15 |  |  |  | 142.7143 | L calf | 3 | 13
14 | L. Upper arm | 122.0238 | 0.41941 | 121.2 | 122.8 | [28 empty] | 144.6095 | R calf | 4 | 14
15 | R. Upper arm | 129.6095 | 0.43348 | 128.9 | 130.4 |  |  |  | z |  |  | x | [13 empty] | z |  |  | x |  |  |  |  | 153.3714 | L foot | 1 | 15
16 | Chest | 117.0429 | 0.35577 | 116.5 | 117.5 | [28 empty] | 159.6714 | R foot | 2 | 16
17 | Back | 110.6857 | 0.59857 | 109.7 | 112.1 | [6 empty] | Corresponding zones on MANIKIN2 and 3 | [21 empty] | 110.6857 | Lo. back | 17 | 17
18 | All | 122.3429 | 0.33552 | 121.6 | 122.8 | [28 empty] | 112.9095 | Seat | 7 | 18
| Temperatures: |  | Fluke Helios Plus 2287A with 40 Thermocouple Channels.
| Position |  | Temperatures (ºC) |  |  |  | Coordinates |  |  |  | 1095-1115
|  | ta [ºC] | STD [ºC] | Min | Max | x | y | z | [23 empty] | a | b | T=ax+b
1 | Vertical 1 | 19.6738 | 0.068132 | 19.5811 | 19.8235 | -1.08 | 0.2 | 0.6 |  |  | 19.648 | 19.721 | 19.672 | 19.733 | 19.791 | 19.721 | 19.705 | 19.635 | 19.656 | 19.567 | 19.604 | 19.64 | 19.555 | 19.551 | 19.625 | 19.674 | 19.658 | 19.612 | 19.56 | 19.572 | 19.547 | 0.9933 | 0.1651 |  | 19.6815 | 19.754 | 19.7053 | 19.7659 | 19.8235 | 19.754 | 19.7381 | 19.6685 | 19.6894 | 19.601 | 19.6378 | 19.6735 | 19.5891 | 19.5851 | 19.6586 | 19.7073 | 19.6914 | 19.6457 | 19.594 | 19.606 | 19.5811
2 | Vertical 2 | 19.9045 | 0.048542 | 19.8189 | 20.0066 | -1.08 | 0.4 | 0.6 |  |  | 19.868 | 19.929 | 19.88 | 19.929 | 19.975 | 19.99 | 19.95 | 19.917 | 19.901 | 19.897 | 19.897 | 19.861 | 19.836 | 19.857 | 19.881 | 19.881 | 19.878 | 19.845 | 19.829 | 19.829 | 19.801 | 0.9932 | 0.1525 |  | 19.8854 | 19.946 | 19.8973 | 19.946 | 19.9917 | 20.0066 | 19.9668 | 19.9341 | 19.9182 | 19.9142 | 19.9142 | 19.8784 | 19.8536 | 19.8745 | 19.8983 | 19.8983 | 19.8953 | 19.8626 | 19.8467 | 19.8467 | 19.8189
3 | Vertical 3 | 20.0376 | 0.053222 | 19.9493 | 20.1473 | -1.08 | 0.6 | 0.6 |  |  | 20.052 | 20.064 | 20.027 | 20.064 | 20.118 | 20.159 | 20.143 | 20.1 | 20.06 | 20.102 | 20.069 | 20.044 | 20.02 | 20.028 | 20.004 | 20.004 | 20.013 | 20.028 | 20 | 19.964 | 19.96 | 0.9951 | 0.0871 |  | 20.0408 | 20.0528 | 20.016 | 20.0528 | 20.1065 | 20.1473 | 20.1314 | 20.0886 | 20.0488 | 20.0906 | 20.0578 | 20.0329 | 20.009 | 20.017 | 19.9931 | 19.9931 | 20.002 | 20.017 | 19.9891 | 19.9533 | 19.9493
4 | Vertical 4 | 20.1494 | 0.084703 | 20.0205 | 20.3439 | -1.08 | 0.8 | 0.6 |  |  | 20.134 | 20.159 | 20.11 | 20.207 | 20.253 | 20.342 | 20.302 | 20.256 | 20.085 | 20.212 | 20.139 | 20.115 | 20.115 | 20.123 | 20.053 | 20.016 | 20.074 | 20.102 | 20.098 | 20.062 | 20.107 | 0.9922 | 0.1606 |  | 20.1376 | 20.1624 | 20.1137 | 20.21 | 20.2556 | 20.3439 | 20.3042 | 20.2586 | 20.0889 | 20.2149 | 20.1425 | 20.1187 | 20.1187 | 20.1266 | 20.0572 | 20.0205 | 20.078 | 20.1058 | 20.1018 | 20.0661 | 20.1108
5 | Vertical 5 | 20.3151 | 0.099805 | 20.1375 | 20.5281 | -1.08 | 1 | 0.6 |  |  | 20.44 | 20.44 | 20.379 | 20.465 | 20.559 | 20.636 | 20.608 | 20.538 | 20.424 | 20.494 | 20.433 | 20.372 | 20.359 | 20.368 | 20.246 | 20.282 | 20.328 | 20.368 | 20.377 | 20.377 | 20.397 | 1.0015 | -0.1389 |  | 20.3318 | 20.3318 | 20.2707 | 20.3568 | 20.4509 | 20.5281 | 20.5 | 20.4299 | 20.3157 | 20.3858 | 20.3247 | 20.2637 | 20.2506 | 20.2597 | 20.1375 | 20.1735 | 20.2196 | 20.2597 | 20.2687 | 20.2687 | 20.2887
6 | Vertical 6 | 20.4738 | 0.080805 | 20.37 | 20.6205 | -1.08 | 1.2 | 0.6 |  |  | 20.599 | 20.599 | 20.538 | 20.575 | 20.666 | 20.66 | 20.69 | 20.648 | 20.485 | 20.543 | 20.531 | 20.543 | 20.531 | 20.601 | 20.441 | 20.478 | 20.438 | 20.441 | 20.475 | 20.45 | 20.459 | 0.994 | 0.0546 |  | 20.53 | 20.53 | 20.4694 | 20.5062 | 20.5966 | 20.5906 | 20.6205 | 20.5787 | 20.4167 | 20.4743 | 20.4624 | 20.4743 | 20.4624 | 20.532 | 20.373 | 20.4097 | 20.37 | 20.373 | 20.4067 | 20.3819 | 20.3908
7 | Vertical 7 | 20.6515 | 0.054814 | 20.56 | 20.7297 | -1.08 | 1.4 | 0.6 |  |  | 20.755 | 20.78 | 20.706 | 20.718 | 20.776 | 20.767 | 20.776 | 20.755 | 20.69 | 20.687 | 20.711 | 20.736 | 20.674 | 20.708 | 20.613 | 20.649 | 20.609 | 20.625 | 20.634 | 20.692 | 20.664 | 0.9922 | 0.1118 |  | 20.7049 | 20.7297 | 20.6563 | 20.6682 | 20.7257 | 20.7168 | 20.7257 | 20.7049 | 20.6404 | 20.6374 | 20.6613 | 20.6861 | 20.6245 | 20.6583 | 20.564 | 20.5997 | 20.56 | 20.5759 | 20.5849 | 20.6424 | 20.6146
8 | Vertical 8 | 20.7445 | 0.040181 | 20.6821 | 20.8163 | -1.08 | 1.6 | 0.6 |  |  | 20.939 | 20.927 | 20.878 | 20.841 | 20.886 | 20.902 | 20.911 | 20.89 | 20.899 | 20.883 | 20.858 | 20.895 | 20.809 | 20.842 | 20.818 | 20.818 | 20.826 | 20.805 | 20.826 | 20.888 | 20.872 | 1.0008 | -0.1395 |  | 20.8163 | 20.8042 | 20.7552 | 20.7182 | 20.7632 | 20.7792 | 20.7882 | 20.7672 | 20.7762 | 20.7602 | 20.7352 | 20.7722 | 20.6861 | 20.7192 | 20.6952 | 20.6952 | 20.7032 | 20.6821 | 20.7032 | 20.7652 | 20.7492
9 | Vertical 9 | 20.7728 | 0.028553 | 20.7246 | 20.8338 | -1.08 | 1.8 | 0.6 |  |  | 20.939 | 20.976 | 20.963 | 20.927 | 20.947 | 20.927 | 20.935 | 20.914 | 20.935 | 20.919 | 20.883 | 20.907 | 20.883 | 20.867 | 20.916 | 20.891 | 20.9 | 20.879 | 20.888 | 20.9 | 20.921 | 1.0022 | -0.1883 |  | 20.7968 | 20.8338 | 20.8208 | 20.7847 | 20.8048 | 20.7847 | 20.7928 | 20.7717 | 20.7928 | 20.7767 | 20.7406 | 20.7647 | 20.7406 | 20.7246 | 20.7737 | 20.7487 | 20.7577 | 20.7366 | 20.7457 | 20.7577 | 20.7787
10 | Vertical 10 | 20.774 | 0.02935 | 20.7057 | 20.8265 | -1.08 | 2 | 0.6 |  |  | 20.927 | 20.963 | 20.988 | 20.976 | 20.984 | 20.963 | 20.96 | 20.927 | 20.935 | 20.919 | 20.919 | 20.932 | 20.919 | 20.867 | 20.928 | 20.928 | 20.949 | 20.903 | 20.9 | 20.924 | 20.933 | 0.9986 | -0.1321 |  | 20.7656 | 20.8016 | 20.8265 | 20.8145 | 20.8225 | 20.8016 | 20.7986 | 20.7656 | 20.7736 | 20.7576 | 20.7576 | 20.7706 | 20.7576 | 20.7057 | 20.7666 | 20.7666 | 20.7876 | 20.7416 | 20.7386 | 20.7626 | 20.7716
11 | Vertical 11 | 20.7833 | 0.032042 | 20.7268 | 20.8435 | -1.08 | 2.2 | 0.6 |  |  | 20.939 | 20.976 | 21 | 20.988 | 20.988 | 20.963 | 20.951 | 20.927 | 20.935 | 20.932 | 20.932 | 20.907 | 20.919 | 20.883 | 20.965 | 20.952 | 20.94 | 20.903 | 20.9 | 20.9 | 20.933 | 0.9974 | -0.1019 |  | 20.7827 | 20.8196 | 20.8435 | 20.8315 | 20.8315 | 20.8066 | 20.7946 | 20.7707 | 20.7787 | 20.7757 | 20.7757 | 20.7507 | 20.7627 | 20.7268 | 20.8086 | 20.7956 | 20.7837 | 20.7468 | 20.7438 | 20.7438 | 20.7767
12 | Vertical 12 | 20.7824 | 0.035901 | 20.7265 | 20.8436 | -1.08 | 2.4 | 0.6 |  |  | 20.988 | 21.024 | 21.012 | 21.012 | 21.012 | 21.012 | 20.988 | 20.963 | 20.935 | 20.956 | 20.956 | 20.932 | 20.944 | 20.907 | 20.94 | 20.965 | 20.952 | 20.952 | 20.924 | 20.912 | 20.933 | 1.0013 | -0.2077 |  | 20.8076 | 20.8436 | 20.8316 | 20.8316 | 20.8316 | 20.8316 | 20.8076 | 20.7826 | 20.7545 | 20.7755 | 20.7755 | 20.7515 | 20.7635 | 20.7265 | 20.7595 | 20.7846 | 20.7715 | 20.7715 | 20.7435 | 20.7315 | 20.7525
13 | Vertical 13 | 19.2465 | 0.086099 | 19.1028 | 19.3769 | 2.19 | 0.2 | 0.25 |  |  | 19.369 | 19.381 | 19.406 | 19.394 | 19.455 | 19.455 | 19.467 | 19.43 | 19.329 | 19.325 | 19.191 | 19.191 | 19.252 | 19.203 | 19.322 | 19.334 | 19.285 | 19.322 | 19.367 | 19.22 | 19.351 | 0.9932 | 0.0423 |  | 19.2796 | 19.2915 | 19.3163 | 19.3044 | 19.365 | 19.365 | 19.3769 | 19.3402 | 19.2399 | 19.2359 | 19.1028 | 19.1028 | 19.1634 | 19.1147 | 19.2329 | 19.2448 | 19.1962 | 19.2329 | 19.2776 | 19.1316 | 19.2617
14 | Vertical 14 | 20.1232 | 0.035822 | 20.0398 | 20.1719 | 2.19 | 0.4 | 0.25 |  |  | 20.269 | 20.256 | 20.22 | 20.195 | 20.269 | 20.269 | 20.256 | 20.256 | 20.192 | 20.237 | 20.212 | 20.188 | 20.2 | 20.237 | 20.209 | 20.136 | 20.184 | 20.221 | 20.242 | 20.181 | 20.189 | 0.9934 | 0.0367 |  | 20.1719 | 20.159 | 20.1232 | 20.0984 | 20.1719 | 20.1719 | 20.159 | 20.159 | 20.0954 | 20.1401 | 20.1153 | 20.0915 | 20.1034 | 20.1401 | 20.1123 | 20.0398 | 20.0875 | 20.1242 | 20.1451 | 20.0845 | 20.0925
15 | Vertical 15 | 20.5548 | 0.039113 | 20.496 | 20.6259 | 2.19 | 0.6 | 0.25 |  |  | 20.743 | 20.755 | 20.731 | 20.718 | 20.743 | 20.706 | 20.706 | 20.706 | 20.678 | 20.687 | 20.674 | 20.674 | 20.662 | 20.674 | 20.649 | 20.625 | 20.649 | 20.671 | 20.646 | 20.634 | 20.63 | 0.9998 | -0.1249 |  | 20.614 | 20.6259 | 20.602 | 20.589 | 20.614 | 20.577 | 20.577 | 20.577 | 20.549 | 20.558 | 20.545 | 20.545 | 20.533 | 20.545 | 20.52 | 20.496 | 20.52 | 20.542 | 20.517 | 20.505 | 20.501
16 | Vertical 16 | 20.5949 | 0.057005 | 20.5095 | 20.6989 | 2.19 | 0.8 | 0.25 |  |  | 20.743 | 20.767 | 20.706 | 20.669 | 20.767 | 20.682 | 20.718 | 20.731 | 20.657 | 20.629 | 20.641 | 20.653 | 20.629 | 20.662 | 20.637 | 20.576 | 20.588 | 20.613 | 20.585 | 20.621 | 20.63 | 0.9912 | 0.1146 |  | 20.6751 | 20.6989 | 20.6384 | 20.6017 | 20.6989 | 20.6146 | 20.6503 | 20.6632 | 20.5898 | 20.5621 | 20.574 | 20.5859 | 20.5621 | 20.5948 | 20.57 | 20.5095 | 20.5214 | 20.5462 | 20.5185 | 20.5541 | 20.5631
17 | Vertical 17 | 20.7267 | 0.045721 | 20.6527 | 20.8254 | 2.19 | 1 | 0.25 |  |  | 20.865 | 20.902 | 20.841 | 20.829 | 20.878 | 20.804 | 20.841 | 20.841 | 20.813 | 20.772 | 20.772 | 20.797 | 20.785 | 20.797 | 20.793 | 20.744 | 20.757 | 20.757 | 20.728 | 20.765 | 20.774 | 0.9928 | 0.0739 |  | 20.7887 | 20.8254 | 20.7648 | 20.7529 | 20.8016 | 20.7281 | 20.7648 | 20.7648 | 20.737 | 20.6963 | 20.6963 | 20.7212 | 20.7092 | 20.7212 | 20.7172 | 20.6685 | 20.6814 | 20.6814 | 20.6527 | 20.6894 | 20.6983
18 | Vertical 18 | 20.818 | 0.038287 | 20.7444 | 20.8928 | 2.19 | 1.2 | 0.25 |  |  | 20.963 | 20.988 | 20.963 | 20.951 | 20.976 | 20.927 | 20.939 | 20.927 | 20.911 | 20.883 | 20.895 | 20.907 | 20.895 | 20.895 | 20.891 | 20.891 | 20.891 | 20.891 | 20.839 | 20.875 | 20.872 | 0.996 | -0.0112 |  | 20.8679 | 20.8928 | 20.8679 | 20.856 | 20.8809 | 20.8321 | 20.844 | 20.8321 | 20.8162 | 20.7883 | 20.8002 | 20.8122 | 20.8002 | 20.8002 | 20.7962 | 20.7962 | 20.7962 | 20.7962 | 20.7444 | 20.7803 | 20.7773
19 | Vertical 19 | 20.7596 | 0.044532 | 20.6977 | 20.8584 | 2.19 | 1.4 | 0.25 |  |  | 20.89 | 20.939 | 20.878 | 20.878 | 20.902 | 20.878 | 20.878 | 20.878 | 20.837 | 20.785 | 20.797 | 20.834 | 20.809 | 20.821 | 20.818 | 20.793 | 20.805 | 20.818 | 20.777 | 20.802 | 20.81 | 0.9919 | 0.089 |  | 20.8098 | 20.8584 | 20.7979 | 20.7979 | 20.8217 | 20.7979 | 20.7979 | 20.7979 | 20.7572 | 20.7056 | 20.7175 | 20.7542 | 20.7294 | 20.7413 | 20.7384 | 20.7136 | 20.7255 | 20.7384 | 20.6977 | 20.7225 | 20.7304
20 | Vertical 20 | 20.8176 | 0.044349 | 20.7586 | 20.8994 | 2.19 | 1.6 | 0.25 |  |  | 20.963 | 20.976 | 20.976 | 20.976 | 21 | 20.951 | 20.963 | 20.951 | 20.899 | 20.858 | 20.883 | 20.919 | 20.895 | 20.883 | 20.891 | 20.879 | 20.879 | 20.903 | 20.863 | 20.875 | 20.884 | 0.9916 | 0.0758 |  | 20.8627 | 20.8756 | 20.8756 | 20.8756 | 20.8994 | 20.8508 | 20.8627 | 20.8508 | 20.7992 | 20.7586 | 20.7834 | 20.8191 | 20.7953 | 20.7834 | 20.7913 | 20.7794 | 20.7794 | 20.8032 | 20.7636 | 20.7754 | 20.7844
21 | Vertical 21 | 20.7043 | 0.044887 | 20.6107 | 20.7742 | 2.19 | 1.8 | 0.25 |  |  | 20.623 | 20.636 | 20.644 | 20.644 | 20.657 | 20.641 | 20.653 | 20.665 | 20.564 | 20.588 | 20.585 | 20.572 | 20.572 | 20.569 | 20.569 | 20.569 | 20.577 | 20.565 | 20.553 | 20.537 | 20.5 | 0.9907 | 0.3014 |  | 20.7326 | 20.7455 | 20.7534 | 20.7534 | 20.7663 | 20.7504 | 20.7623 | 20.7742 | 20.6742 | 20.6979 | 20.695 | 20.6821 | 20.6821 | 20.6791 | 20.6791 | 20.6791 | 20.687 | 20.6751 | 20.6633 | 20.6474 | 20.6107
22 | Vertical 22 | 20.7199 | 0.044537 | 20.6327 | 20.7855 | 2.19 | 2 | 0.25 |  |  | 20.721 | 20.734 | 20.73 | 20.742 | 20.742 | 20.751 | 20.739 | 20.726 | 20.674 | 20.649 | 20.646 | 20.682 | 20.67 | 20.654 | 20.654 | 20.667 | 20.675 | 20.651 | 20.663 | 20.623 | 20.598 | 0.9991 | 0.0532 |  | 20.7556 | 20.7685 | 20.7645 | 20.7765 | 20.7765 | 20.7855 | 20.7735 | 20.7605 | 20.7086 | 20.6836 | 20.6806 | 20.7166 | 20.7046 | 20.6886 | 20.6886 | 20.7016 | 20.7096 | 20.6856 | 20.6976 | 20.6576 | 20.6327
23 | Vertical 23 | 20.7229 | 0.042288 | 20.642 | 20.7941 | 2.19 | 2.2 | 0.25 |  |  | 20.697 | 20.685 | 20.706 | 20.718 | 20.73 | 20.739 | 20.726 | 20.714 | 20.662 | 20.649 | 20.634 | 20.658 | 20.658 | 20.654 | 20.618 | 20.642 | 20.651 | 20.626 | 20.639 | 20.623 | 20.586 | 0.994 | 0.1795 |  | 20.7523 | 20.7404 | 20.7613 | 20.7732 | 20.7851 | 20.7941 | 20.7811 | 20.7692 | 20.7175 | 20.7046 | 20.6897 | 20.7136 | 20.7136 | 20.7096 | 20.6738 | 20.6976 | 20.7066 | 20.6817 | 20.6947 | 20.6788 | 20.642
24 | Vertical 24 | 20.7212 | 0.042071 | 20.6225 | 20.7875 | 2.19 | 2.4 | 0.25 |  |  | 20.697 | 20.697 | 20.706 | 20.706 | 20.73 | 20.739 | 20.726 | 20.726 | 20.674 | 20.674 | 20.646 | 20.67 | 20.67 | 20.667 | 20.642 | 20.642 | 20.651 | 20.626 | 20.639 | 20.623 | 20.574 | 0.9999 | 0.0506 |  | 20.7455 | 20.7455 | 20.7545 | 20.7545 | 20.7785 | 20.7875 | 20.7745 | 20.7745 | 20.7225 | 20.7225 | 20.6945 | 20.7185 | 20.7185 | 20.7155 | 20.6905 | 20.6905 | 20.6995 | 20.6745 | 20.6875 | 20.6715 | 20.6225
25 | Air 0.1 | 19.2399 | 0.096187 | 19.0687 | 19.43 | 1.22 | 0.1 | 1.1 |  |  | 19.213 | 19.237 | 19.099 | 19.099 | 19.111 | 19.255 | 19.313 | 19.23 | 19.117 | 19.178 | 19.027 | 19.125 | 19.101 | 18.95 | 18.999 | 18.987 | 19.179 | 19.142 | 19.142 | 19.004 | 19.053 | 0.9952 | 0.2097 |  | 19.3305 | 19.3544 | 19.217 | 19.217 | 19.229 | 19.3723 | 19.43 | 19.3474 | 19.2349 | 19.2956 | 19.1454 | 19.2429 | 19.219 | 19.0687 | 19.1175 | 19.1056 | 19.2966 | 19.2598 | 19.2598 | 19.1225 | 19.1712
26 | Air 0.6 | 20.1407 | 0.03124 | 20.0804 | 20.1987 | 1.22 | 0.6 | 1.1 |  |  | 20.113 | 20.1 | 20.084 | 20.084 | 20.133 | 20.093 | 20.105 | 20.105 | 20.077 | 20.102 | 20.074 | 20.074 | 20.037 | 20.07 | 20.07 | 20.033 | 20.066 | 20.066 | 20.054 | 20.014 | 20.014 | 0.994 | 0.1865 |  | 20.1788 | 20.1659 | 20.15 | 20.15 | 20.1987 | 20.1589 | 20.1709 | 20.1709 | 20.143 | 20.1679 | 20.1401 | 20.1401 | 20.1033 | 20.1361 | 20.1361 | 20.0993 | 20.1321 | 20.1321 | 20.1202 | 20.0804 | 20.0804
27 | Air 1.1 | 20.5555 | 0.065068 | 20.4515 | 20.6557 | 1.22 | 1.1 | 1.1 |  |  | 20.599 | 20.587 | 20.546 | 20.51 | 20.595 | 20.531 | 20.567 | 20.592 | 20.515 | 20.49 | 20.462 | 20.475 | 20.438 | 20.52 | 20.471 | 20.41 | 20.418 | 20.418 | 20.394 | 20.464 | 20.464 | 0.9962 | 0.135 |  | 20.6557 | 20.6438 | 20.6029 | 20.5671 | 20.6517 | 20.588 | 20.6238 | 20.6488 | 20.572 | 20.5471 | 20.5192 | 20.5322 | 20.4953 | 20.577 | 20.5282 | 20.4674 | 20.4754 | 20.4754 | 20.4515 | 20.5212 | 20.5212
28 | Air 1.5 | 20.7703 | 0.053677 | 20.6861 | 20.85 | 1.22 | 1.5 | 1.1 |  |  | 20.746 | 20.758 | 20.767 | 20.779 | 20.779 | 20.739 | 20.763 | 20.763 | 20.686 | 20.637 | 20.658 | 20.695 | 20.67 | 20.654 | 20.679 | 20.642 | 20.663 | 20.663 | 20.614 | 20.647 | 20.672 | 0.9935 | 0.2061 |  | 20.8173 | 20.8292 | 20.8381 | 20.85 | 20.85 | 20.8103 | 20.8341 | 20.8341 | 20.7576 | 20.709 | 20.7298 | 20.7666 | 20.7417 | 20.7258 | 20.7507 | 20.7139 | 20.7348 | 20.7348 | 20.6861 | 20.7189 | 20.7437
29 | Cieling | 20.7684 | 0.038358 | 20.7081 | 20.8352 | 0 | 2.46 | 0.6 |  |  | 20.77 | 20.77 | 20.779 | 20.779 | 20.779 | 20.8 | 20.775 | 20.763 | 20.711 | 20.711 | 20.695 | 20.719 | 20.707 | 20.716 | 20.716 | 20.728 | 20.724 | 20.7 | 20.7 | 20.672 | 20.672 | 0.9933 | 0.1746 |  | 20.8054 | 20.8054 | 20.8144 | 20.8144 | 20.8144 | 20.8352 | 20.8104 | 20.7985 | 20.7468 | 20.7468 | 20.7309 | 20.7548 | 20.7429 | 20.7518 | 20.7518 | 20.7637 | 20.7597 | 20.7359 | 20.7359 | 20.7081 | 20.7081
30 | Floor | 20.9765 | 0.028624 | 20.9387 | 21.017 | 1.85 | 0 | 0.6 |  |  | 20.954 | 20.966 | 20.95 | 20.963 | 20.963 | 20.959 | 20.971 | 20.959 | 20.943 | 20.955 | 20.915 | 20.915 | 20.915 | 20.911 | 20.911 | 20.899 | 20.908 | 20.896 | 20.896 | 20.892 | 20.892 | 0.9921 | 0.2117 |  | 21.0002 | 21.0121 | 20.9962 | 21.0091 | 21.0091 | 21.0051 | 21.017 | 21.0051 | 20.9893 | 21.0012 | 20.9615 | 20.9615 | 20.9615 | 20.9575 | 20.9575 | 20.9456 | 20.9545 | 20.9426 | 20.9426 | 20.9387 | 20.9387
31 | Floor | 24.3759 | 0.028865 | 24.3387 | 24.4421 | 0.59 | 0 | 0.6 |  |  | 24.322 | 24.322 | 24.307 | 24.342 | 24.354 | 24.386 | 24.363 | 24.347 | 24.335 | 24.347 | 24.3 | 24.296 | 24.296 | 24.293 | 24.304 | 24.325 | 24.316 | 24.281 | 24.289 | 24.285 | 24.285 | 0.9847 | 0.4292 |  | 24.3791 | 24.3791 | 24.3643 | 24.3988 | 24.4106 | 24.4421 | 24.4194 | 24.4037 | 24.3919 | 24.4037 | 24.3574 | 24.3535 | 24.3535 | 24.3505 | 24.3613 | 24.382 | 24.3732 | 24.3387 | 24.3466 | 24.3426 | 24.3426
32 | Floor | 19.9478 | 0.039104 | 19.8846 | 20.012 | 0 | 0 | 0.6 |  |  | 19.892 | 19.905 | 19.901 | 19.938 | 19.938 | 19.946 | 19.934 | 19.918 | 19.906 | 19.894 | 19.869 | 19.841 | 19.866 | 19.862 | 19.85 | 19.871 | 19.837 | 19.837 | 19.834 | 19.818 | 19.855 | 0.9948 | 0.1697 |  | 19.9583 | 19.9712 | 19.9672 | 20.004 | 20.004 | 20.012 | 20 | 19.9841 | 19.9722 | 19.9603 | 19.9354 | 19.9075 | 19.9324 | 19.9284 | 19.9165 | 19.9374 | 19.9035 | 19.9035 | 19.9006 | 19.8846 | 19.9215
33 | Mid cieling | 20.9069 | 0.026894 | 20.869 | 20.9518 | 1.22 | 2.46 | 0.6 |  |  | 20.88 | 20.88 | 20.889 | 20.877 | 20.865 | 20.873 | 20.861 | 20.858 | 20.858 | 20.845 | 20.845 | 20.829 | 20.829 | 20.826 | 20.826 | 20.822 | 20.813 | 20.813 | 20.822 | 20.806 | 20.806 | 0.9972 | 0.1213 |  | 20.9428 | 20.9428 | 20.9518 | 20.9398 | 20.9279 | 20.9359 | 20.9239 | 20.9209 | 20.9209 | 20.9079 | 20.9079 | 20.892 | 20.892 | 20.889 | 20.889 | 20.885 | 20.876 | 20.876 | 20.885 | 20.869 | 20.869
34 | Window wall | 21.0868 | 0.027114 | 21.0512 | 21.1249 | 0.59 | 1.23 | 1.2 |  |  | 21.049 | 21.049 | 21.033 | 21.045 | 21.045 | 21.042 | 21.029 | 21.026 | 21.014 | 21.026 | 21.014 | 20.998 | 20.998 | 20.994 | 20.994 | 20.978 | 20.982 | 20.982 | 20.978 | 20.975 | 20.975 | 0.9966 | 0.1475 |  | 21.1249 | 21.1249 | 21.109 | 21.1209 | 21.1209 | 21.118 | 21.105 | 21.102 | 21.0901 | 21.102 | 21.0901 | 21.0741 | 21.0741 | 21.0701 | 21.0701 | 21.0542 | 21.0582 | 21.0582 | 21.0542 | 21.0512 | 21.0512
35 | Window wall | 21.0567 | 0.021841 | 21.0205 | 21.0911 | 1.85 | 1.23 | 1.2 |  |  | 21 | 21.012 | 20.996 | 21.008 | 21.008 | 21.005 | 20.993 | 20.989 | 20.977 | 20.977 | 20.977 | 20.964 | 20.964 | 20.97 | 20.97 | 20.957 | 20.96 | 20.96 | 20.957 | 20.941 | 20.941 | 0.9957 | 0.1695 |  | 21.0792 | 21.0911 | 21.0752 | 21.0872 | 21.0872 | 21.0842 | 21.0722 | 21.0682 | 21.0563 | 21.0563 | 21.0563 | 21.0434 | 21.0434 | 21.0493 | 21.0493 | 21.0364 | 21.0394 | 21.0394 | 21.0364 | 21.0205 | 21.0205
36 | Door wall | 20.4893 | 0.030361 | 20.439 | 20.5361 | 1.85 | 1.23 | 0 |  |  | 20.394 | 20.406 | 20.39 | 20.403 | 20.378 | 20.387 | 20.387 | 20.383 | 20.359 | 20.371 | 20.359 | 20.343 | 20.355 | 20.339 | 20.351 | 20.323 | 20.339 | 20.315 | 20.323 | 20.32 | 20.308 | 0.9912 | 0.3097 |  | 20.5242 | 20.5361 | 20.5203 | 20.5332 | 20.5084 | 20.5173 | 20.5173 | 20.5133 | 20.4895 | 20.5014 | 20.4895 | 20.4737 | 20.4856 | 20.4697 | 20.4816 | 20.4539 | 20.4697 | 20.4459 | 20.4539 | 20.4509 | 20.439
37 | Door wall | 20.5595 | 0.033883 | 20.5135 | 20.6167 | 0.59 | 1.23 | 0 |  |  | 20.428 | 20.44 | 20.436 | 20.449 | 20.436 | 20.408 | 20.421 | 20.417 | 20.396 | 20.396 | 20.383 | 20.367 | 20.367 | 20.364 | 20.376 | 20.36 | 20.364 | 20.351 | 20.348 | 20.357 | 20.344 | 0.9828 | 0.5194 |  | 20.596 | 20.6078 | 20.6039 | 20.6167 | 20.6039 | 20.5764 | 20.5892 | 20.5852 | 20.5646 | 20.5646 | 20.5518 | 20.5361 | 20.5361 | 20.5331 | 20.5449 | 20.5292 | 20.5331 | 20.5204 | 20.5174 | 20.5263 | 20.5135
38 | Upper outlet | 20.8344 | 0.042227 | 20.7484 | 20.9085 | 2.44 | 1.84 | 0.6 |  |  | 20.709 | 20.783 | 20.791 | 20.779 | 20.767 | 20.739 | 20.726 | 20.735 | 20.698 | 20.698 | 20.711 | 20.67 | 20.707 | 20.63 | 20.74 | 20.724 | 20.728 | 20.667 | 20.675 | 20.66 | 20.708 | 0.9946 | 0.2298 |  | 20.827 | 20.9006 | 20.9085 | 20.8966 | 20.8847 | 20.8568 | 20.8439 | 20.8528 | 20.816 | 20.816 | 20.829 | 20.7882 | 20.825 | 20.7484 | 20.8578 | 20.8419 | 20.8459 | 20.7852 | 20.7932 | 20.7782 | 20.826
39 | Lower outlet | 20.3533 | 0.098632 | 20.1942 | 20.5411 | 2.44 | 0.63 | 0.6 |  |  | 20.186 | 20.137 | 20.378 | 20.342 | 20.329 | 20.142 | 20.289 | 20.298 | 20.163 | 20.175 | 20.175 | 20.061 | 20.11 | 20.205 | 20.41 | 20.238 | 20.266 | 20.241 | 20.066 | 20.295 | 20.136 | 0.9939 | 0.2556 |  | 20.3185 | 20.2698 | 20.5093 | 20.4735 | 20.4606 | 20.2747 | 20.4208 | 20.4298 | 20.2956 | 20.3075 | 20.3075 | 20.1942 | 20.2429 | 20.3373 | 20.5411 | 20.3701 | 20.398 | 20.3731 | 20.1992 | 20.4268 | 20.2688
40 | Back wall | 21.0046 | 0.030596 | 20.9598 | 21.0466 | 2.44 | 1.23 | 0.6 |  |  | 20.942 | 20.942 | 20.938 | 20.938 | 20.938 | 20.922 | 20.922 | 20.919 | 20.906 | 20.906 | 20.906 | 20.878 | 20.891 | 20.887 | 20.887 | 20.871 | 20.862 | 20.862 | 20.871 | 20.855 | 20.855 | 0.9974 | 0.159 |  | 21.0466 | 21.0466 | 21.0426 | 21.0426 | 21.0426 | 21.0266 | 21.0266 | 21.0236 | 21.0106 | 21.0106 | 21.0106 | 20.9827 | 20.9957 | 20.9917 | 20.9917 | 20.9757 | 20.9668 | 20.9668 | 20.9757 | 20.9598 | 20.9598
| Air velocities: |  | Dantec Dynamics Indoor Flow System with 5 54T21 Omnidirectional Transducers.
| Position |  | Air velocities (m/s) |  |  |  | Coordinates |  |  |  | 153.5 | 154.9 | 149.8 | 148.3 | 150.1 | 154.6 | 155.3 | 151.1 | 154.8 | 155 | 154.8 | 155.9 | 152.9 | 153.5 | 150.9 | 156.3 | 154.4 | 153.7 | 154.7 | 152.1 | 154.2 |  | L. Foot |  | 153.3714 | 2.1818 | 148.3 | 156.3
|  | va [m/s] | STD [m/s] | Tu % |  | x | y | z |  |  | 160.8 | 161.7 | 157.4 | 156.5 | 156.3 | 158.7 | 159.4 | 158.1 | 160.3 | 161.9 | 160.6 | 161 | 159.7 | 160.5 | 155.9 | 159.8 | 162.2 | 160 | 162.4 | 160.2 | 159.7 |  | R. Foot |  | 159.6714 | 1.9053 | 155.9 | 162.4
1 | Air vel. 1 | 0.292 | 0.017 | 5.93 |  | 0.19 | 1.3 | 0 |  |  | 142.2 | 142.3 | 141.8 | 141.6 | 142.5 | 143.2 | 143 | 142.5 | 142.6 | 143.1 | 143.2 | 143.9 | 142.7 | 142.6 | 142 | 142.8 | 142.8 | 142.7 | 143.3 | 143.1 | 143.1 |  | L. Low leg |  | 142.7143 | 0.5434 | 141.6 | 143.9
2 | Air vel. 2 | 0.269 | 0.014 | 5.195 |  | 0.19 | 1.1 | 0 |  |  | 143.8 | 144.2 | 142.9 | 142.9 | 144.4 | 145.5 | 145.1 | 143.6 | 144.5 | 145.3 | 145.5 | 146.2 | 144 | 144.5 | 143.5 | 146.1 | 144.8 | 144.8 | 145.1 | 144.6 | 145.5 |  | R. Low leg |  | 144.6095 | 0.9359 | 142.9 | 146.2
3 | Air vel. 3 | 0.254 | 0.01 | 3.815 |  | 0.19 | 0.875 | 0 |  |  | 100.2 | 99.8 | 99.6 | 99.2 | 100.1 | 101.1 | 100.6 | 100.3 | 100.1 | 100.4 | 100.4 | 99.9 | 100 | 99.7 | 99.5 | 100 | 100.1 | 99.8 | 100.3 | 100 | 99.5 |  | L. Thigh |  | 100.0286 | 0.42443 | 99.2 | 101.1
4 | Air vel. 4 | 0.243 | 0.009 | 3.551 |  | 0.19 | 0.55 | 0 |  |  | 104.3 | 104.3 | 104 | 103.1 | 104.4 | 104.7 | 104.5 | 104.6 | 104.2 | 104.7 | 104.8 | 105 | 104.7 | 104.5 | 104.4 | 104.5 | 104.4 | 104.6 | 104.6 | 104.9 | 104.9 |  | R. Thigh |  | 104.481 | 0.40077 | 103.1 | 105
5 | Air vel. 5 | 0.278 | 0.036 | 12.962 |  | 0.19 | 0.275 | 0 |  |  | 112.3 | 111.9 | 112.1 | 113.3 | 113.4 | 114 | 112.7 | 113.1 | 112.8 | 113.4 | 113.4 | 113.2 | 112.3 | 112.7 | 114.1 | 113.1 | 112.4 | 112.6 | 112.8 | 112.7 | 112.8 |  | Pelvis |  | 112.9095 | 0.5735 | 111.9 | 114.1
6 | Air vel. 6 | 0.186 | 0.077 | 41.344 |  | 2.19 | 1.3 | 0 |  |  | 118.4 | 118.7 | 119.1 | 118.7 | 118.9 | 119.7 | 119.2 | 119.1 | 119.9 | 119.5 | 119.6 | 120 | 119.8 | 119.7 | 120.1 | 120.3 | 119.7 | 119.9 | 120.1 | 119.2 | 119.5 |  | Head |  | 119.481 | 0.52404 | 118.4 | 120.3
7 | Air vel. 7 | 0.228 | 0.057 | 24.867 |  | 2.19 | 1.1 | 0 |  |  | 71.1 | 71.2 | 71.8 | 70.8 | 71.1 | 71.6 | 71.2 | 71.4 | 71.7 | 71.7 | 72 | 71.8 | 71.5 | 71.6 | 72.3 | 72.7 | 72.1 | 71.8 | 72 | 71.4 | 71.6 |  | Top of head |  | 71.6381 | 0.44326 | 70.8 | 72.7
8 | Air vel. 8 | 0.72 | 0.053 | 7.357 |  | 2.19 | 0.875 | 0 |  |  | 163.6 | 162.8 | 163.8 | 162.5 | 162.3 | 162 | 162.7 | 162.9 | 163.1 | 162.1 | 162.4 | 162.7 | 162.8 | 162.2 | 163.7 | 163.2 | 163.7 | 163.7 | 164 | 164.1 | 163.4 |  | L. Hand |  | 163.0333 | 0.65904 | 162 | 164.1
9 | Air vel. 9 | 0.982 | 0.043 | 4.383 |  | 2.19 | 0.55 | 0 |  |  | 185.9 | 185.1 | 182.9 | 182.3 | 184.9 | 186 | 186.3 | 185.6 | 184.7 | 185.5 | 184.7 | 186.3 | 185.6 | 184.9 | 182.3 | 184.9 | 185.9 | 186.6 | 186.5 | 186.4 | 185.9 |  | R. Hand |  | 185.2 | 1.283 | 182.3 | 186.6
10 | Air vel. 10 | 0.469 | 0.032 | 6.849 |  | 2.19 | 0.275 | 0 |  |  | 153.9 | 153.8 | 154.1 | 150.8 | 150.9 | 151 | 151.9 | 152.3 | 153.2 | 152.5 | 152.8 | 152.9 | 153.4 | 152.7 | 153.1 | 154 | 154.6 | 153.8 | 154.5 | 153.6 | 153.3 |  | L. Forearm |  | 153.0048 | 1.1205 | 150.8 | 154.6
[11 empty] | 131.5 | 130.1 | 128.8 | 131.5 | 131.9 | 132.8 | 133 | 132.5 | 129.8 | 131.6 | 131 | 131.4 | 129.8 | 129.8 | 130.3 | 129.8 | 129.6 | 131 | 130.7 | 131.6 | 131.3 |  | R. Forearm |  | 130.9429 | 1.1325 | 128.8 | 133
[11 empty] | 121.7 | 122 | 121.5 | 121.6 | 122 | 122.4 | 121.9 | 121.7 | 122.4 | 122.4 | 122.1 | 122.2 | 121.6 | 122.2 | 121.5 | 122.5 | 121.2 | 122.8 | 122.5 | 122.4 | 121.9 |  | L. Upper arm |  | 122.0238 | 0.41941 | 121.2 | 122.8
[11 empty] | 129.8 | 129.2 | 128.9 | 129.7 | 129.1 | 129 | 130.1 | 130.1 | 129.7 | 129.6 | 129.8 | 130.1 | 129.4 | 129.2 | 130.4 | 129.5 | 129.1 | 130.2 | 129.7 | 129.9 | 129.3 |  | R. Upper arm |  | 129.6095 | 0.43348 | 128.9 | 130.4
[11 empty] | 116.8 | 116.5 | 116.8 | 116.6 | 116.9 | 116.7 | 116.7 | 117.2 | 117.5 | 116.9 | 116.9 | 117.1 | 116.7 | 116.6 | 117.4 | 117.3 | 117.5 | 117.4 | 117.5 | 117.5 | 117.4 |  | Chest |  | 117.0429 | 0.35577 | 116.5 | 117.5
[11 empty] | 110.2 | 109.8 | 110.9 | 112.1 | 110.9 | 110.5 | 110.7 | 110.7 | 110.6 | 110.5 | 111.1 | 110.5 | 109.7 | 109.9 | 111.4 | 111.2 | 109.9 | 110.7 | 110.5 | 111.3 | 111.3 |  | Back |  | 110.6857 | 0.59857 | 109.7 | 112.1
[11 empty] | 122.2 | 122 | 121.7 | 121.6 | 122 | 122.6 | 122.5 | 122.3 | 122.4 | 122.6 | 122.6 | 122.8 | 122.1 | 122.1 | 122.2 | 122.7 | 122.4 | 122.5 | 122.8 | 122.6 | 122.5 |  | All |  | 122.3429 | 0.33552 | 121.6 | 122.8

## HL2@va0.27ta20
Manikin heat loss in windtunnel
| Nom. Inlet velocity |  | 0.2 | m/s | Nom. Air temperature |  | 20 | ºC
| Mean Inlet velocity |  | 0.2672 | m/s | Mean Air temp. |  | 20.4223 | ºC
[10 empty] | 1 |  | 2 | [15 empty] | 2
| Std. dev. Inlet vel. |  | 0.0172 | m/s | Std. dev. Air temp. |  | 0.059757 | ºC
1
| Mean Inlet Turb. intens. |  | 6.2906 | % | Mean Wall temp. |  | 21.0798 | ºC
| Relative Humidity |  | 35 | % | Air Pressure |  | 1027.15 | mbar | 4 |  |  | 3 | [12 empty] | 6 | [6 empty] | 5
| Thermal manikin: |  | Comfortina, No clothing, Software version 3.0.30. | [6 empty] | 6 | [17 empty] | 3
| Body Segments |  | Heat loss (W/m2) | [30 empty] | H L (W/m2) | Zones | No
|  | Q [W/m2] | STD [W/m2] | Min | Max | [7 empty] | 8 |  |  |  | 10 | [7 empty] | 10 | [6 empty] | 11 |  | 122.5571 | Total | 18
1 | L. Foot | 151.8429 | 2.8532 | 147.7 | 158.3 | [28 empty] | 71.6524 | Scalp | 9 | 1
2 | R. Foot | 158.6762 | 2.0978 | 154.4 | 163.3 |  |  |  |  | 17 | [23 empty] | 119.3095 | Face | 8 | 2
3 | L. Low leg | 143.2143 | 0.6311 | 141.9 | 144.2 | [28 empty] | 117.3333 | Chest | 16 | 3
4 | R. Low leg | 144.4333 | 1.1137 | 142 | 146.6 | [5 empty] | 18 |  |  |  |  | 12 | [9 empty] | 12 |  | 18 |  | 11 |  |  |  | 111.2238 | Up. back | 17 | 4
5 | L. Thigh | 100.3333 | 0.40415 | 99.6 | 101 | [28 empty] | 122.1905 | L U arm | 14 | 5
6 | R. Thigh | 104.6524 | 0.47288 | 103.1 | 105.5 | [28 empty] | 130.1952 | R U arm | 15 | 6
7 | Pelvis | 113.3714 | 0.51686 | 112.2 | 114 | [28 empty] | 152.6714 | L L arm | 12 | 7
8 | Head | 119.3095 | 0.55128 | 118.5 | 120.3 | [28 empty] | 132.5619 | R L arm | 13 | 8
9 | Top of head | 71.6524 | 0.50261 | 70.6 | 72.8 | [14 empty] | 14 | [5 empty] | 14 |  |  |  | 13 |  |  |  | 163.2524 | L hand | 10 | 9
10 | L. Hand | 163.2524 | 0.91357 | 161.6 | 165 | [28 empty] | 185.8429 | R hand | 11 | 10
11 | R. Hand | 185.8429 | 0.97702 | 183.6 | 187.6 | [28 empty] | 100.3333 | L thigh | 5 | 11
12 | L. Forearm | 152.6714 | 1.4329 | 150.2 | 154.8 |  |  |  | y | [19 empty] | y |  |  |  |  | 104.6524 | R thigh | 6 | 12
13 | R. Forearm | 132.5619 | 1.4246 | 128.5 | 134.3 | [14 empty] | 16 | [5 empty] | 16 |  |  |  | 15 |  |  |  | 143.2143 | L calf | 3 | 13
14 | L. Upper arm | 122.1905 | 0.74425 | 121.1 | 123.9 | [28 empty] | 144.4333 | R calf | 4 | 14
15 | R. Upper arm | 130.1952 | 0.67489 | 129.1 | 131.8 |  |  |  | z |  |  | x | [13 empty] | z |  |  | x |  |  |  |  | 151.8429 | L foot | 1 | 15
16 | Chest | 117.3333 | 0.30876 | 116.6 | 117.9 | [28 empty] | 158.6762 | R foot | 2 | 16
17 | Back | 111.2238 | 0.85727 | 109.6 | 112.5 | [6 empty] | Corresponding zones on MANIKIN2 and 3 | [21 empty] | 111.2238 | Lo. back | 17 | 17
18 | All | 122.5571 | 0.42845 | 121.7 | 123.4 | [28 empty] | 113.3714 | Seat | 7 | 18
| Temperatures: |  | Fluke Helios Plus 2287A with 40 Thermocouple Channels.
| Position |  | Temperatures (ºC) |  |  |  | Coordinates |  |  |  | 1210-1230
|  | ta [ºC] | STD [ºC] | Min | Max | x | y | z | [23 empty] | a | b | T=ax+b
1 | Vertical 1 | 19.664 | 0.073847 | 19.4997 | 19.754 | -1.08 | 0.2 | 0.6 |  |  | 19.665 | 19.639 | 19.639 | 19.66 | 19.709 | 19.721 | 19.696 | 19.705 | 19.693 | 19.668 | 19.717 | 19.522 | 19.567 | 19.555 | 19.49 | 19.465 | 19.6 | 19.637 | 19.649 | 19.596 | 19.645 | 0.9933 | 0.1651 |  | 19.6983 | 19.6725 | 19.6725 | 19.6934 | 19.742 | 19.754 | 19.7291 | 19.7381 | 19.7262 | 19.7013 | 19.75 | 19.5563 | 19.601 | 19.5891 | 19.5245 | 19.4997 | 19.6338 | 19.6705 | 19.6825 | 19.6298 | 19.6785
2 | Vertical 2 | 19.8763 | 0.057705 | 19.7891 | 19.9827 | -1.08 | 0.4 | 0.6 |  |  | 19.922 | 19.872 | 19.847 | 19.892 | 19.941 | 19.966 | 19.929 | 19.95 | 19.901 | 19.864 | 19.852 | 19.803 | 19.812 | 19.824 | 19.796 | 19.771 | 19.808 | 19.845 | 19.832 | 19.78 | 19.829 | 0.9932 | 0.1525 |  | 19.939 | 19.8894 | 19.8645 | 19.9092 | 19.9579 | 19.9827 | 19.946 | 19.9668 | 19.9182 | 19.8814 | 19.8695 | 19.8208 | 19.8298 | 19.8417 | 19.8139 | 19.7891 | 19.8258 | 19.8626 | 19.8496 | 19.798 | 19.8467
3 | Vertical 3 | 20.0322 | 0.092695 | 19.9045 | 20.204 | -1.08 | 0.6 | 0.6 |  |  | 20.103 | 20.04 | 20.04 | 20.015 | 20.183 | 20.207 | 20.146 | 20.216 | 20.167 | 20.106 | 20.02 | 19.962 | 19.959 | 19.971 | 19.967 | 19.967 | 19.979 | 19.992 | 19.967 | 19.915 | 19.988 | 0.9951 | 0.0871 |  | 20.0916 | 20.0289 | 20.0289 | 20.004 | 20.1712 | 20.1951 | 20.1344 | 20.204 | 20.1553 | 20.0946 | 20.009 | 19.9513 | 19.9483 | 19.9602 | 19.9563 | 19.9563 | 19.9682 | 19.9811 | 19.9563 | 19.9045 | 19.9772
4 | Vertical 4 | 20.1792 | 0.12167 | 20.0125 | 20.4045 | -1.08 | 0.8 | 0.6 |  |  | 20.188 | 20.223 | 20.236 | 20.183 | 20.367 | 20.403 | 20.244 | 20.388 | 20.326 | 20.253 | 20.082 | 20.02 | 20.008 | 20.102 | 20.111 | 20.074 | 20.087 | 20.074 | 20.087 | 20.034 | 20.205 | 0.9922 | 0.1606 |  | 20.1911 | 20.2259 | 20.2388 | 20.1862 | 20.3687 | 20.4045 | 20.2467 | 20.3896 | 20.3281 | 20.2556 | 20.086 | 20.0244 | 20.0125 | 20.1058 | 20.1147 | 20.078 | 20.0909 | 20.078 | 20.0909 | 20.0383 | 20.208
5 | Vertical 5 | 20.3531 | 0.11941 | 20.1525 | 20.5611 | -1.08 | 1 | 0.6 |  |  | 20.507 | 20.566 | 20.505 | 20.513 | 20.62 | 20.669 | 20.538 | 20.617 | 20.58 | 20.534 | 20.449 | 20.375 | 20.261 | 20.323 | 20.294 | 20.356 | 20.343 | 20.368 | 20.356 | 20.389 | 20.524 | 1.0015 | -0.1389 |  | 20.3989 | 20.4579 | 20.3969 | 20.4049 | 20.512 | 20.5611 | 20.4299 | 20.509 | 20.472 | 20.4259 | 20.3408 | 20.2667 | 20.1525 | 20.2146 | 20.1855 | 20.2476 | 20.2346 | 20.2597 | 20.2476 | 20.2807 | 20.4159
6 | Vertical 6 | 20.5313 | 0.078017 | 20.3859 | 20.6364 | -1.08 | 1.2 | 0.6 |  |  | 20.601 | 20.685 | 20.587 | 20.645 | 20.706 | 20.706 | 20.633 | 20.678 | 20.666 | 20.666 | 20.666 | 20.605 | 20.518 | 20.577 | 20.454 | 20.49 | 20.478 | 20.539 | 20.515 | 20.548 | 20.643 | 0.994 | 0.0546 |  | 20.532 | 20.6155 | 20.5181 | 20.5757 | 20.6364 | 20.6364 | 20.5638 | 20.6085 | 20.5966 | 20.5966 | 20.5966 | 20.536 | 20.4495 | 20.5081 | 20.3859 | 20.4217 | 20.4097 | 20.4704 | 20.4465 | 20.4793 | 20.5737
7 | Vertical 7 | 20.6811 | 0.040791 | 20.6057 | 20.7377 | -1.08 | 1.4 | 0.6 |  |  | 20.761 | 20.759 | 20.747 | 20.755 | 20.755 | 20.755 | 20.78 | 20.764 | 20.776 | 20.776 | 20.788 | 20.727 | 20.687 | 20.723 | 20.671 | 20.708 | 20.683 | 20.695 | 20.671 | 20.655 | 20.716 | 0.9922 | 0.1118 |  | 20.7109 | 20.7089 | 20.697 | 20.7049 | 20.7049 | 20.7049 | 20.7297 | 20.7138 | 20.7257 | 20.7257 | 20.7377 | 20.6771 | 20.6374 | 20.6732 | 20.6216 | 20.6583 | 20.6335 | 20.6454 | 20.6216 | 20.6057 | 20.6662
8 | Vertical 8 | 20.7452 | 0.02355 | 20.7162 | 20.8002 | -1.08 | 1.6 | 0.6 |  |  | 20.895 | 20.869 | 20.869 | 20.865 | 20.841 | 20.841 | 20.865 | 20.874 | 20.874 | 20.862 | 20.923 | 20.886 | 20.883 | 20.895 | 20.867 | 20.903 | 20.854 | 20.842 | 20.842 | 20.839 | 20.839 | 1.0008 | -0.1395 |  | 20.7722 | 20.7462 | 20.7462 | 20.7422 | 20.7182 | 20.7182 | 20.7422 | 20.7512 | 20.7512 | 20.7392 | 20.8002 | 20.7632 | 20.7602 | 20.7722 | 20.7442 | 20.7802 | 20.7312 | 20.7192 | 20.7192 | 20.7162 | 20.7162
9 | Vertical 9 | 20.7531 | 0.030301 | 20.7196 | 20.8138 | -1.08 | 1.8 | 0.6 |  |  | 20.92 | 20.893 | 20.869 | 20.89 | 20.865 | 20.865 | 20.865 | 20.862 | 20.886 | 20.886 | 20.947 | 20.911 | 20.932 | 20.956 | 20.928 | 20.94 | 20.879 | 20.879 | 20.879 | 20.888 | 20.863 | 1.0022 | -0.1883 |  | 20.7777 | 20.7507 | 20.7266 | 20.7477 | 20.7226 | 20.7226 | 20.7226 | 20.7196 | 20.7436 | 20.7436 | 20.8048 | 20.7687 | 20.7898 | 20.8138 | 20.7857 | 20.7978 | 20.7366 | 20.7366 | 20.7366 | 20.7457 | 20.7206
10 | Vertical 10 | 20.7491 | 0.030295 | 20.7007 | 20.7946 | -1.08 | 2 | 0.6 |  |  | 20.944 | 20.906 | 20.893 | 20.914 | 20.89 | 20.878 | 20.865 | 20.862 | 20.886 | 20.886 | 20.947 | 20.935 | 20.956 | 20.956 | 20.952 | 20.94 | 20.891 | 20.903 | 20.903 | 20.924 | 20.888 | 0.9986 | -0.1321 |  | 20.7826 | 20.7446 | 20.7316 | 20.7526 | 20.7287 | 20.7167 | 20.7037 | 20.7007 | 20.7247 | 20.7247 | 20.7856 | 20.7736 | 20.7946 | 20.7946 | 20.7906 | 20.7786 | 20.7297 | 20.7416 | 20.7416 | 20.7626 | 20.7267
11 | Vertical 11 | 20.7473 | 0.026497 | 20.6969 | 20.7996 | -1.08 | 2.2 | 0.6 |  |  | 20.956 | 20.93 | 20.918 | 20.902 | 20.89 | 20.878 | 20.853 | 20.862 | 20.886 | 20.886 | 20.923 | 20.907 | 20.932 | 20.932 | 20.919 | 20.919 | 20.891 | 20.903 | 20.9 | 20.924 | 20.863 | 0.9974 | -0.1019 |  | 20.7996 | 20.7737 | 20.7617 | 20.7458 | 20.7338 | 20.7218 | 20.6969 | 20.7059 | 20.7298 | 20.7298 | 20.7667 | 20.7507 | 20.7757 | 20.7757 | 20.7627 | 20.7627 | 20.7348 | 20.7468 | 20.7438 | 20.7677 | 20.7069
12 | Vertical 12 | 20.7559 | 0.022305 | 20.7075 | 20.8126 | -1.08 | 2.4 | 0.6 |  |  | 20.993 | 20.967 | 20.955 | 20.951 | 20.951 | 20.927 | 20.927 | 20.911 | 20.935 | 20.911 | 20.923 | 20.919 | 20.919 | 20.944 | 20.944 | 20.944 | 20.928 | 20.94 | 20.949 | 20.937 | 20.888 | 1.0013 | -0.2077 |  | 20.8126 | 20.7866 | 20.7745 | 20.7705 | 20.7705 | 20.7465 | 20.7465 | 20.7305 | 20.7545 | 20.7305 | 20.7425 | 20.7385 | 20.7385 | 20.7635 | 20.7635 | 20.7635 | 20.7475 | 20.7595 | 20.7685 | 20.7565 | 20.7075
13 | Vertical 13 | 19.3218 | 0.094836 | 19.1147 | 19.4713 | 2.19 | 0.2 | 0.25 |  |  | 19.506 | 19.529 | 19.504 | 19.513 | 19.562 | 19.476 | 19.443 | 19.402 | 19.473 | 19.463 | 19.497 | 19.35 | 19.203 | 19.313 | 19.276 | 19.313 | 19.334 | 19.358 | 19.404 | 19.367 | 19.355 | 0.9932 | 0.0423 |  | 19.4157 | 19.4385 | 19.4137 | 19.4226 | 19.4713 | 19.3859 | 19.3531 | 19.3124 | 19.3829 | 19.373 | 19.4067 | 19.2607 | 19.1147 | 19.224 | 19.1872 | 19.224 | 19.2448 | 19.2687 | 19.3144 | 19.2776 | 19.2657
14 | Vertical 14 | 20.1284 | 0.084857 | 19.9991 | 20.2564 | 2.19 | 0.4 | 0.25 |  |  | 20.299 | 20.248 | 20.272 | 20.256 | 20.342 | 20.354 | 20.33 | 20.314 | 20.326 | 20.277 | 20.216 | 20.2 | 20.212 | 20.188 | 20.151 | 20.176 | 20.099 | 20.111 | 20.107 | 20.095 | 20.156 | 0.9934 | 0.0367 |  | 20.2017 | 20.1511 | 20.1749 | 20.159 | 20.2444 | 20.2564 | 20.2325 | 20.2166 | 20.2285 | 20.1799 | 20.1193 | 20.1034 | 20.1153 | 20.0915 | 20.0547 | 20.0795 | 20.003 | 20.015 | 20.011 | 19.9991 | 20.0597
15 | Vertical 15 | 20.5461 | 0.050086 | 20.453 | 20.619 | 2.19 | 0.6 | 0.25 |  |  | 20.748 | 20.722 | 20.698 | 20.694 | 20.743 | 20.718 | 20.731 | 20.703 | 20.727 | 20.69 | 20.678 | 20.65 | 20.674 | 20.674 | 20.638 | 20.662 | 20.622 | 20.61 | 20.582 | 20.582 | 20.631 | 0.9998 | -0.1249 |  | 20.619 | 20.593 | 20.569 | 20.565 | 20.614 | 20.589 | 20.602 | 20.574 | 20.598 | 20.561 | 20.549 | 20.521 | 20.545 | 20.545 | 20.509 | 20.533 | 20.493 | 20.481 | 20.453 | 20.453 | 20.502
16 | Vertical 16 | 20.6116 | 0.056081 | 20.5155 | 20.6989 | 2.19 | 0.8 | 0.25 |  |  | 20.699 | 20.734 | 20.734 | 20.718 | 20.767 | 20.718 | 20.755 | 20.727 | 20.727 | 20.715 | 20.703 | 20.625 | 20.601 | 20.65 | 20.613 | 20.613 | 20.634 | 20.622 | 20.582 | 20.643 | 20.679 | 0.9912 | 0.1146 |  | 20.6314 | 20.6661 | 20.6661 | 20.6503 | 20.6989 | 20.6503 | 20.687 | 20.6592 | 20.6592 | 20.6473 | 20.6354 | 20.5581 | 20.5343 | 20.5829 | 20.5462 | 20.5462 | 20.567 | 20.5551 | 20.5155 | 20.5759 | 20.6116
17 | Vertical 17 | 20.7274 | 0.038625 | 20.6606 | 20.7887 | 2.19 | 1 | 0.25 |  |  | 20.846 | 20.857 | 20.832 | 20.829 | 20.865 | 20.829 | 20.853 | 20.825 | 20.825 | 20.813 | 20.813 | 20.772 | 20.772 | 20.809 | 20.736 | 20.76 | 20.769 | 20.769 | 20.741 | 20.777 | 20.777 | 0.9928 | 0.0739 |  | 20.7698 | 20.7807 | 20.7559 | 20.7529 | 20.7887 | 20.7529 | 20.7768 | 20.749 | 20.749 | 20.737 | 20.737 | 20.6963 | 20.6963 | 20.7331 | 20.6606 | 20.6844 | 20.6934 | 20.6934 | 20.6656 | 20.7013 | 20.7013
18 | Vertical 18 | 20.8006 | 0.026508 | 20.7634 | 20.849 | 2.19 | 1.2 | 0.25 |  |  | 20.944 | 20.93 | 20.918 | 20.914 | 20.939 | 20.914 | 20.914 | 20.898 | 20.911 | 20.911 | 20.886 | 20.87 | 20.883 | 20.895 | 20.858 | 20.883 | 20.879 | 20.867 | 20.863 | 20.863 | 20.863 | 0.996 | -0.0112 |  | 20.849 | 20.8351 | 20.8231 | 20.8191 | 20.844 | 20.8191 | 20.8191 | 20.8032 | 20.8162 | 20.8162 | 20.7913 | 20.7753 | 20.7883 | 20.8002 | 20.7634 | 20.7883 | 20.7843 | 20.7723 | 20.7683 | 20.7683 | 20.7683
19 | Vertical 19 | 20.7567 | 0.0251 | 20.7056 | 20.7979 | 2.19 | 1.4 | 0.25 |  |  | 20.859 | 20.869 | 20.869 | 20.865 | 20.878 | 20.853 | 20.865 | 20.837 | 20.837 | 20.837 | 20.85 | 20.821 | 20.809 | 20.834 | 20.785 | 20.821 | 20.818 | 20.818 | 20.802 | 20.826 | 20.814 | 0.9919 | 0.089 |  | 20.779 | 20.789 | 20.789 | 20.785 | 20.7979 | 20.7731 | 20.785 | 20.7572 | 20.7572 | 20.7572 | 20.7701 | 20.7413 | 20.7294 | 20.7542 | 20.7056 | 20.7413 | 20.7384 | 20.7384 | 20.7225 | 20.7463 | 20.7344
20 | Vertical 20 | 20.8066 | 0.020699 | 20.7636 | 20.8439 | 2.19 | 1.6 | 0.25 |  |  | 20.944 | 20.942 | 20.942 | 20.927 | 20.927 | 20.914 | 20.914 | 20.898 | 20.911 | 20.898 | 20.898 | 20.883 | 20.883 | 20.907 | 20.895 | 20.895 | 20.891 | 20.903 | 20.9 | 20.9 | 20.863 | 0.9916 | 0.0758 |  | 20.8439 | 20.8419 | 20.8419 | 20.827 | 20.827 | 20.8141 | 20.8141 | 20.7983 | 20.8111 | 20.7983 | 20.7983 | 20.7834 | 20.7834 | 20.8072 | 20.7953 | 20.7953 | 20.7913 | 20.8032 | 20.8002 | 20.8002 | 20.7636
21 | Vertical 21 | 20.6743 | 0.024906 | 20.6236 | 20.7306 | 2.19 | 1.8 | 0.25 |  |  | 20.621 | 20.595 | 20.579 | 20.607 | 20.595 | 20.566 | 20.579 | 20.564 | 20.552 | 20.539 | 20.548 | 20.564 | 20.548 | 20.548 | 20.557 | 20.541 | 20.544 | 20.557 | 20.565 | 20.565 | 20.513 | 0.9907 | 0.3014 |  | 20.7306 | 20.7049 | 20.689 | 20.7168 | 20.7049 | 20.6761 | 20.689 | 20.6742 | 20.6623 | 20.6494 | 20.6583 | 20.6742 | 20.6583 | 20.6583 | 20.6672 | 20.6514 | 20.6543 | 20.6672 | 20.6751 | 20.6751 | 20.6236
22 | Vertical 22 | 20.6931 | 0.025483 | 20.6327 | 20.7416 | 2.19 | 2 | 0.25 |  |  | 20.707 | 20.693 | 20.689 | 20.68 | 20.656 | 20.652 | 20.652 | 20.674 | 20.637 | 20.662 | 20.646 | 20.662 | 20.646 | 20.646 | 20.691 | 20.639 | 20.618 | 20.655 | 20.663 | 20.663 | 20.598 | 0.9991 | 0.0532 |  | 20.7416 | 20.7276 | 20.7236 | 20.7146 | 20.6906 | 20.6866 | 20.6866 | 20.7086 | 20.6716 | 20.6966 | 20.6806 | 20.6966 | 20.6806 | 20.6806 | 20.7256 | 20.6736 | 20.6526 | 20.6896 | 20.6976 | 20.6976 | 20.6327
23 | Vertical 23 | 20.6885 | 0.02085 | 20.6301 | 20.7235 | 2.19 | 2.2 | 0.25 |  |  | 20.658 | 20.668 | 20.652 | 20.656 | 20.631 | 20.615 | 20.603 | 20.649 | 20.625 | 20.625 | 20.634 | 20.649 | 20.621 | 20.621 | 20.642 | 20.639 | 20.618 | 20.63 | 20.639 | 20.639 | 20.574 | 0.994 | 0.1795 |  | 20.7136 | 20.7235 | 20.7076 | 20.7116 | 20.6867 | 20.6708 | 20.6589 | 20.7046 | 20.6807 | 20.6807 | 20.6897 | 20.7046 | 20.6768 | 20.6768 | 20.6976 | 20.6947 | 20.6738 | 20.6857 | 20.6947 | 20.6947 | 20.6301
24 | Vertical 24 | 20.6843 | 0.021562 | 20.6225 | 20.7185 | 2.19 | 2.4 | 0.25 |  |  | 20.67 | 20.668 | 20.652 | 20.656 | 20.631 | 20.628 | 20.615 | 20.662 | 20.625 | 20.637 | 20.634 | 20.637 | 20.621 | 20.621 | 20.655 | 20.639 | 20.618 | 20.642 | 20.639 | 20.626 | 20.574 | 0.9999 | 0.0506 |  | 20.7185 | 20.7165 | 20.7005 | 20.7045 | 20.6795 | 20.6765 | 20.6635 | 20.7105 | 20.6735 | 20.6855 | 20.6825 | 20.6855 | 20.6695 | 20.6695 | 20.7035 | 20.6875 | 20.6665 | 20.6905 | 20.6875 | 20.6745 | 20.6225
25 | Air 0.1 | 19.2753 | 0.091198 | 19.1145 | 19.4449 | 1.22 | 0.1 | 1.1 |  |  | 19.195 | 19.147 | 19.263 | 19.254 | 19.328 | 19.3 | 19.193 | 19.117 | 19.092 | 19.248 | 19.174 | 19.211 | 19.113 | 19.064 | 19.158 | 19.057 | 19.024 | 19.204 | 19.106 | 18.996 | 19.065 | 0.9952 | 0.2097 |  | 19.3126 | 19.2648 | 19.3802 | 19.3713 | 19.4449 | 19.4171 | 19.3106 | 19.2349 | 19.2101 | 19.3653 | 19.2917 | 19.3285 | 19.231 | 19.1822 | 19.2757 | 19.1752 | 19.1424 | 19.3215 | 19.224 | 19.1145 | 19.1832
26 | Air 0.6 | 20.1198 | 0.056613 | 20.0347 | 20.2285 | 1.22 | 0.6 | 1.1 |  |  | 20.073 | 20.084 | 20.068 | 20.084 | 20.12 | 20.153 | 20.117 | 20.163 | 20.09 | 20.053 | 20.061 | 20.053 | 20.037 | 20.037 | 20.009 | 20.005 | 19.972 | 19.972 | 19.968 | 19.993 | 20.014 | 0.994 | 0.1865 |  | 20.1391 | 20.15 | 20.1341 | 20.15 | 20.1858 | 20.2186 | 20.1828 | 20.2285 | 20.156 | 20.1192 | 20.1271 | 20.1192 | 20.1033 | 20.1033 | 20.0754 | 20.0715 | 20.0387 | 20.0387 | 20.0347 | 20.0595 | 20.0804
27 | Air 1.1 | 20.5674 | 0.063613 | 20.4635 | 20.6517 | 1.22 | 1.1 | 1.1 |  |  | 20.511 | 20.57 | 20.566 | 20.546 | 20.595 | 20.566 | 20.566 | 20.576 | 20.564 | 20.576 | 20.56 | 20.478 | 20.413 | 20.487 | 20.434 | 20.443 | 20.422 | 20.434 | 20.406 | 20.492 | 20.513 | 0.9962 | 0.135 |  | 20.5681 | 20.6268 | 20.6228 | 20.6029 | 20.6517 | 20.6228 | 20.6228 | 20.6328 | 20.6209 | 20.6328 | 20.6169 | 20.5352 | 20.4704 | 20.5441 | 20.4914 | 20.5003 | 20.4794 | 20.4914 | 20.4635 | 20.5491 | 20.5701
28 | Air 1.5 | 20.765 | 0.024912 | 20.707 | 20.8023 | 1.22 | 1.5 | 1.1 |  |  | 20.731 | 20.729 | 20.726 | 20.729 | 20.705 | 20.713 | 20.677 | 20.698 | 20.662 | 20.674 | 20.695 | 20.674 | 20.67 | 20.682 | 20.703 | 20.688 | 20.679 | 20.679 | 20.7 | 20.712 | 20.635 | 0.9935 | 0.2061 |  | 20.8023 | 20.8004 | 20.7974 | 20.8004 | 20.7765 | 20.7845 | 20.7487 | 20.7696 | 20.7338 | 20.7457 | 20.7666 | 20.7457 | 20.7417 | 20.7537 | 20.7745 | 20.7596 | 20.7507 | 20.7507 | 20.7716 | 20.7835 | 20.707
29 | Cieling | 20.7339 | 0.026062 | 20.6833 | 20.7905 | 0 | 2.46 | 0.6 |  |  | 20.755 | 20.741 | 20.726 | 20.729 | 20.717 | 20.689 | 20.701 | 20.711 | 20.686 | 20.674 | 20.695 | 20.686 | 20.658 | 20.682 | 20.691 | 20.7 | 20.679 | 20.679 | 20.712 | 20.7 | 20.647 | 0.9933 | 0.1746 |  | 20.7905 | 20.7766 | 20.7617 | 20.7647 | 20.7528 | 20.725 | 20.7369 | 20.7468 | 20.722 | 20.7101 | 20.7309 | 20.722 | 20.6942 | 20.718 | 20.727 | 20.7359 | 20.7151 | 20.7151 | 20.7478 | 20.7359 | 20.6833
30 | Floor | 20.8902 | 0.019059 | 20.8533 | 20.9228 | 1.85 | 0 | 0.6 |  |  | 20.866 | 20.864 | 20.86 | 20.876 | 20.864 | 20.86 | 20.848 | 20.87 | 20.821 | 20.821 | 20.842 | 20.845 | 20.842 | 20.842 | 20.838 | 20.834 | 20.826 | 20.826 | 20.822 | 20.834 | 20.806 | 0.9921 | 0.2117 |  | 20.9129 | 20.9109 | 20.9069 | 20.9228 | 20.9109 | 20.9069 | 20.895 | 20.9168 | 20.8682 | 20.8682 | 20.889 | 20.892 | 20.889 | 20.889 | 20.8851 | 20.8811 | 20.8732 | 20.8732 | 20.8692 | 20.8811 | 20.8533
31 | Floor | 24.3399 | 0.02671 | 24.2845 | 24.3771 | 0.59 | 0 | 0.6 |  |  | 24.296 | 24.306 | 24.309 | 24.282 | 24.294 | 24.311 | 24.282 | 24.288 | 24.276 | 24.3 | 24.32 | 24.317 | 24.284 | 24.296 | 24.293 | 24.257 | 24.257 | 24.253 | 24.241 | 24.226 | 24.238 | 0.9847 | 0.4292 |  | 24.3535 | 24.3633 | 24.3663 | 24.3397 | 24.3515 | 24.3682 | 24.3397 | 24.3456 | 24.3338 | 24.3574 | 24.3771 | 24.3741 | 24.3417 | 24.3535 | 24.3505 | 24.3151 | 24.3151 | 24.3111 | 24.2993 | 24.2845 | 24.2964
32 | Floor | 19.9251 | 0.043217 | 19.8677 | 20.015 | 0 | 0 | 0.6 |  |  | 19.853 | 19.888 | 19.904 | 19.888 | 19.949 | 19.86 | 19.875 | 19.869 | 19.881 | 19.906 | 19.93 | 19.878 | 19.804 | 19.841 | 19.801 | 19.801 | 19.813 | 19.822 | 19.822 | 19.83 | 19.818 | 0.9948 | 0.1697 |  | 19.9195 | 19.9543 | 19.9702 | 19.9543 | 20.015 | 19.9264 | 19.9413 | 19.9354 | 19.9473 | 19.9722 | 19.9961 | 19.9443 | 19.8707 | 19.9075 | 19.8677 | 19.8677 | 19.8797 | 19.8886 | 19.8886 | 19.8966 | 19.8846
33 | Mid cieling | 20.8536 | 0.019476 | 20.8202 | 20.881 | 1.22 | 2.46 | 0.6 |  |  | 20.817 | 20.815 | 20.818 | 20.803 | 20.815 | 20.811 | 20.803 | 20.809 | 20.784 | 20.796 | 20.784 | 20.78 | 20.78 | 20.793 | 20.789 | 20.777 | 20.765 | 20.773 | 20.761 | 20.77 | 20.757 | 0.9972 | 0.1213 |  | 20.88 | 20.878 | 20.881 | 20.8661 | 20.878 | 20.874 | 20.8661 | 20.872 | 20.8471 | 20.8591 | 20.8471 | 20.8431 | 20.8431 | 20.8561 | 20.8521 | 20.8401 | 20.8282 | 20.8361 | 20.8242 | 20.8331 | 20.8202
34 | Window wall | 21.0419 | 0.025424 | 20.9894 | 21.0841 | 0.59 | 1.23 | 1.2 |  |  | 20.997 | 20.983 | 20.999 | 21.008 | 20.995 | 20.992 | 20.983 | 20.977 | 20.965 | 20.965 | 20.965 | 20.961 | 20.949 | 20.973 | 20.957 | 20.945 | 20.945 | 20.941 | 20.941 | 20.913 | 20.926 | 0.9966 | 0.1475 |  | 21.0731 | 21.0592 | 21.0751 | 21.0841 | 21.0711 | 21.0681 | 21.0592 | 21.0532 | 21.0412 | 21.0412 | 21.0412 | 21.0372 | 21.0253 | 21.0492 | 21.0332 | 21.0213 | 21.0213 | 21.0173 | 21.0173 | 20.9894 | 21.0024
35 | Window wall | 20.9993 | 0.018554 | 20.9687 | 21.0274 | 1.85 | 1.23 | 1.2 |  |  | 20.948 | 20.946 | 20.938 | 20.934 | 20.946 | 20.931 | 20.934 | 20.928 | 20.916 | 20.928 | 20.916 | 20.912 | 20.912 | 20.924 | 20.921 | 20.908 | 20.908 | 20.893 | 20.893 | 20.889 | 20.889 | 0.9957 | 0.1695 |  | 21.0274 | 21.0254 | 21.0175 | 21.0135 | 21.0254 | 21.0105 | 21.0135 | 21.0075 | 20.9956 | 21.0075 | 20.9956 | 20.9916 | 20.9916 | 21.0035 | 21.0005 | 20.9876 | 20.9876 | 20.9727 | 20.9727 | 20.9687 | 20.9687
36 | Door wall | 20.4256 | 0.027267 | 20.3775 | 20.4717 | 1.85 | 1.23 | 0 |  |  | 20.339 | 20.328 | 20.32 | 20.316 | 20.341 | 20.313 | 20.316 | 20.298 | 20.298 | 20.298 | 20.285 | 20.294 | 20.282 | 20.294 | 20.29 | 20.29 | 20.266 | 20.262 | 20.262 | 20.246 | 20.246 | 0.9912 | 0.3097 |  | 20.4697 | 20.4588 | 20.4509 | 20.4469 | 20.4717 | 20.4439 | 20.4469 | 20.4291 | 20.4291 | 20.4291 | 20.4162 | 20.4251 | 20.4132 | 20.4251 | 20.4211 | 20.4211 | 20.3974 | 20.3934 | 20.3934 | 20.3775 | 20.3775
37 | Door wall | 20.5086 | 0.025433 | 20.4653 | 20.5567 | 0.59 | 1.23 | 0 |  |  | 20.388 | 20.374 | 20.366 | 20.362 | 20.374 | 20.358 | 20.362 | 20.343 | 20.343 | 20.343 | 20.334 | 20.331 | 20.331 | 20.34 | 20.315 | 20.315 | 20.315 | 20.311 | 20.311 | 20.308 | 20.295 | 0.9828 | 0.5194 |  | 20.5567 | 20.543 | 20.5351 | 20.5312 | 20.543 | 20.5272 | 20.5312 | 20.5125 | 20.5125 | 20.5125 | 20.5037 | 20.5007 | 20.5007 | 20.5096 | 20.485 | 20.485 | 20.485 | 20.4811 | 20.4811 | 20.4781 | 20.4653
38 | Upper outlet | 20.8117 | 0.048506 | 20.6927 | 20.9135 | 2.44 | 1.84 | 0.6 |  |  | 20.792 | 20.705 | 20.696 | 20.705 | 20.68 | 20.664 | 20.631 | 20.686 | 20.662 | 20.662 | 20.796 | 20.695 | 20.731 | 20.719 | 20.691 | 20.679 | 20.667 | 20.675 | 20.724 | 20.733 | 20.574 | 0.9946 | 0.2298 |  | 20.9095 | 20.823 | 20.814 | 20.823 | 20.7981 | 20.7822 | 20.7494 | 20.8041 | 20.7802 | 20.7802 | 20.9135 | 20.813 | 20.8489 | 20.8369 | 20.8091 | 20.7971 | 20.7852 | 20.7932 | 20.8419 | 20.8508 | 20.6927
39 | Lower outlet | 20.3499 | 0.12922 | 20.0849 | 20.5232 | 2.44 | 0.63 | 0.6 |  |  | 20.352 | 20.206 | 20.112 | 20.255 | 20.316 | 20.251 | 20.279 | 20.392 | 20.322 | 20.285 | 20.392 | 19.951 | 20.233 | 20.208 | 20.021 | 20.082 | 20.058 | 20.079 | 20.103 | 20.366 | 20.308 | 0.9939 | 0.2556 |  | 20.4835 | 20.3383 | 20.2449 | 20.387 | 20.4477 | 20.3831 | 20.4109 | 20.5232 | 20.4536 | 20.4169 | 20.5232 | 20.0849 | 20.3652 | 20.3403 | 20.1545 | 20.2151 | 20.1912 | 20.2121 | 20.236 | 20.4974 | 20.4397
40 | Back wall | 20.9518 | 0.027705 | 20.8989 | 20.9927 | 2.44 | 1.23 | 0.6 |  |  | 20.887 | 20.876 | 20.88 | 20.864 | 20.888 | 20.86 | 20.876 | 20.858 | 20.858 | 20.858 | 20.845 | 20.842 | 20.842 | 20.842 | 20.838 | 20.838 | 20.814 | 20.81 | 20.81 | 20.794 | 20.806 | 0.9974 | 0.159 |  | 20.9917 | 20.9807 | 20.9847 | 20.9688 | 20.9927 | 20.9648 | 20.9807 | 20.9628 | 20.9628 | 20.9628 | 20.9498 | 20.9468 | 20.9468 | 20.9468 | 20.9428 | 20.9428 | 20.9189 | 20.9149 | 20.9149 | 20.8989 | 20.9109
| Air velocities: |  | Dantec Dynamics Indoor Flow System with 5 54T21 Omnidirectional Transducers.
| Position |  | Air velocities (m/s) |  |  |  | Coordinates |  |  |  | 147.7 | 150.9 | 149.9 | 151.9 | 155.2 | 153 | 149.3 | 148.6 | 149.5 | 148.2 | 154 | 158.3 | 150.5 | 155.8 | 154.7 | 150.1 | 154.5 | 154.4 | 150.5 | 150.5 | 151.2 |  | L. Foot |  | 151.8429 | 2.8532 | 147.7 | 158.3
|  | va [m/s] | STD [m/s] | Tu % |  | x | y | z |  |  | 154.4 | 158.6 | 158.3 | 159.1 | 159.4 | 158.1 | 156.2 | 156.7 | 157.6 | 155.2 | 159.4 | 163.3 | 157.7 | 161 | 161.1 | 157.4 | 160.3 | 161.2 | 158.9 | 159.2 | 159.1 |  | R. Foot |  | 158.6762 | 2.0978 | 154.4 | 163.3
1 | Air vel. 1 | 0.292 | 0.017 | 5.93 |  | 0.19 | 1.3 | 0 |  |  | 141.9 | 142.7 | 143.2 | 143.4 | 143.2 | 142.5 | 142.6 | 142.8 | 143 | 142.3 | 143.9 | 144.2 | 142.8 | 143.5 | 144.2 | 143.5 | 144.2 | 143.7 | 143.4 | 143.2 | 143.3 |  | L. Low leg |  | 143.2143 | 0.6311 | 141.9 | 144.2
2 | Air vel. 2 | 0.269 | 0.014 | 5.195 |  | 0.19 | 1.1 | 0 |  |  | 142 | 143.5 | 144.2 | 145 | 145.3 | 144.4 | 143 | 143.3 | 144.3 | 143 | 145.7 | 146.6 | 143.8 | 145.5 | 145.4 | 144.2 | 145.7 | 145.4 | 144.4 | 144.2 | 144.2 |  | R. Low leg |  | 144.4333 | 1.1137 | 142 | 146.6
3 | Air vel. 3 | 0.254 | 0.01 | 3.815 |  | 0.19 | 0.875 | 0 |  |  | 100.6 | 100.3 | 99.8 | 100 | 100.7 | 100.1 | 99.6 | 100.3 | 99.9 | 99.6 | 100.3 | 100.4 | 100.1 | 100.5 | 100.7 | 100.2 | 100.7 | 101 | 100.7 | 100.9 | 100.6 |  | L. Thigh |  | 100.3333 | 0.40415 | 99.6 | 101
4 | Air vel. 4 | 0.243 | 0.009 | 3.551 |  | 0.19 | 0.55 | 0 |  |  | 104.5 | 105.1 | 104.7 | 104.3 | 104.9 | 104.5 | 103.1 | 104.4 | 104.7 | 104.5 | 104.7 | 104.6 | 104.6 | 104.7 | 105.2 | 105.5 | 104.9 | 105 | 104.6 | 105 | 104.2 |  | R. Thigh |  | 104.6524 | 0.47288 | 103.1 | 105.5
5 | Air vel. 5 | 0.278 | 0.036 | 12.962 |  | 0.19 | 0.275 | 0 |  |  | 112.4 | 112.2 | 113.2 | 113.4 | 113.5 | 113.9 | 113.4 | 114 | 113.8 | 113.7 | 113.1 | 112.6 | 113.5 | 112.8 | 113.2 | 113.4 | 114 | 113.9 | 113.9 | 113.5 | 113.4 |  | Pelvis |  | 113.3714 | 0.51686 | 112.2 | 114
6 | Air vel. 6 | 0.186 | 0.077 | 41.344 |  | 2.19 | 1.3 | 0 |  |  | 118.5 | 118.6 | 118.7 | 118.5 | 119 | 119.1 | 119.4 | 119.4 | 119.5 | 119.5 | 119.7 | 119.9 | 118.9 | 120.3 | 119.4 | 119.4 | 120.1 | 120.2 | 119.7 | 118.9 | 118.8 |  | Head |  | 119.3095 | 0.55128 | 118.5 | 120.3
7 | Air vel. 7 | 0.228 | 0.057 | 24.867 |  | 2.19 | 1.1 | 0 |  |  | 71.3 | 71.3 | 71.2 | 70.6 | 71 | 71.2 | 71.4 | 71.8 | 71.7 | 71.9 | 72.1 | 71.8 | 71.3 | 72.8 | 72.1 | 71.9 | 72.1 | 72.2 | 72.1 | 71.5 | 71.4 |  | Top of head |  | 71.6524 | 0.50261 | 70.6 | 72.8
8 | Air vel. 8 | 0.72 | 0.053 | 7.357 |  | 2.19 | 0.875 | 0 |  |  | 162.9 | 163.2 | 162.9 | 162.8 | 162 | 161.7 | 161.6 | 162 | 162.6 | 163.6 | 163.8 | 163.2 | 164.1 | 164.4 | 164.1 | 163.6 | 163.7 | 163.9 | 164 | 165 | 163.2 |  | L. Hand |  | 163.2524 | 0.91357 | 161.6 | 165
9 | Air vel. 9 | 0.982 | 0.043 | 4.383 |  | 2.19 | 0.55 | 0 |  |  | 186.3 | 187.2 | 185.6 | 185.5 | 186.3 | 185 | 184.2 | 185.2 | 186.5 | 183.6 | 185.6 | 185.6 | 184.8 | 186.8 | 186.8 | 187.6 | 186.7 | 185.3 | 186.3 | 185.9 | 185.9 |  | R. Hand |  | 185.8429 | 0.97702 | 183.6 | 187.6
10 | Air vel. 10 | 0.469 | 0.032 | 6.849 |  | 2.19 | 0.275 | 0 |  |  | 152.9 | 153.1 | 151.7 | 151.4 | 151 | 151 | 150.2 | 150.5 | 151.2 | 152.8 | 153.9 | 154.8 | 153.9 | 154.5 | 154.1 | 153 | 153 | 154.4 | 153.6 | 153.7 | 151.4 |  | L. Forearm |  | 152.6714 | 1.4329 | 150.2 | 154.8
[11 empty] | 132.5 | 133.7 | 134.3 | 132.7 | 133.3 | 132.8 | 132.5 | 133.8 | 134.1 | 132.1 | 130.8 | 128.5 | 130.5 | 131.7 | 132.3 | 134 | 133.5 | 131 | 133.2 | 133 | 133.5 |  | R. Forearm |  | 132.5619 | 1.4246 | 128.5 | 134.3
[11 empty] | 121.3 | 121.6 | 121.4 | 121.1 | 121.5 | 121.8 | 122 | 122 | 122.6 | 121.9 | 122.9 | 121.9 | 121.7 | 123.3 | 122.4 | 123.3 | 123.9 | 122.8 | 122.8 | 121.9 | 121.9 |  | L. Upper arm |  | 122.1905 | 0.74425 | 121.1 | 123.9
[11 empty] | 129.8 | 130 | 130.4 | 130 | 129.1 | 129.4 | 129.9 | 129.6 | 130.1 | 130.6 | 130.4 | 130.1 | 129.5 | 130.3 | 129.7 | 130.3 | 131.7 | 130.6 | 131.8 | 130.9 | 129.9 |  | R. Upper arm |  | 130.1952 | 0.67489 | 129.1 | 131.8
[11 empty] | 116.8 | 116.6 | 117.3 | 117.2 | 117.3 | 117.1 | 117.5 | 117.1 | 117 | 117.1 | 117.3 | 117.6 | 117.5 | 117.4 | 117.5 | 117.4 | 117.7 | 117.9 | 117.5 | 117.6 | 117.6 |  | Chest |  | 117.3333 | 0.30876 | 116.6 | 117.9
[11 empty] | 110.1 | 110.6 | 111.3 | 110.4 | 109.6 | 110.8 | 111.8 | 111.9 | 111.9 | 112.4 | 111.5 | 109.8 | 110.7 | 111.1 | 111.1 | 110.5 | 112.4 | 111.6 | 112.5 | 112 | 111.7 |  | Back |  | 111.2238 | 0.85727 | 109.6 | 112.5
[11 empty] | 121.7 | 122.2 | 122.3 | 122.3 | 122.5 | 122.3 | 121.9 | 122.3 | 122.5 | 122.2 | 122.8 | 122.8 | 122.3 | 123 | 123 | 122.7 | 123.4 | 123.2 | 123 | 122.8 | 122.5 |  | All |  | 122.5571 | 0.42845 | 121.7 | 123.4

## HL3@va0.27ta20
Manikin heat loss in windtunnel
| Nom. Inlet velocity |  | 0.2 | m/s | Nom. Air temperature |  | 20 | ºC
| Mean Inlet velocity |  | 0.2672 | m/s | Mean Air temp. |  | 20.3956 | ºC
[10 empty] | 1 |  | 2 | [15 empty] | 2
| Std. dev. Inlet vel. |  | 0.0172 | m/s | Std. dev. Air temp. |  | 0.044821 | ºC
1
| Mean Inlet Turb. intens. |  | 6.2906 | % | Mean Wall temp. |  | 21.0199 | ºC
| Relative Humidity |  | 35 | % | Air Pressure |  | 1027.15 | mbar | 4 |  |  | 3 | [12 empty] | 6 | [6 empty] | 5
| Thermal manikin: |  | Comfortina, No clothing, Software version 3.0.30. | [6 empty] | 6 | [17 empty] | 3
| Body Segments |  | Heat loss (W/m2) | [30 empty] | H L (W/m2) | Zones | No
|  | Q [W/m2] | STD [W/m2] | Min | Max | [7 empty] | 8 |  |  |  | 10 | [7 empty] | 10 | [6 empty] | 11 |  | 123.3 | Total | 18
1 | L. Foot | 154.8476 | 2.3505 | 151 | 158.6 | [28 empty] | 71.9619 | Scalp | 9 | 1
2 | R. Foot | 160.4238 | 1.7038 | 156.8 | 163 |  |  |  |  | 17 | [23 empty] | 119.9619 | Face | 8 | 2
3 | L. Low leg | 144.2238 | 0.47635 | 143.2 | 145 | [28 empty] | 117.7524 | Chest | 16 | 3
4 | R. Low leg | 145.5429 | 1.0656 | 143.8 | 147.2 | [5 empty] | 18 |  |  |  |  | 12 | [9 empty] | 12 |  | 18 |  | 11 |  |  |  | 111.5048 | Up. back | 17 | 4
5 | L. Thigh | 101.0095 | 0.34337 | 100.3 | 101.7 | [28 empty] | 122.9095 | L U arm | 14 | 5
6 | R. Thigh | 105.319 | 0.32499 | 104.8 | 105.8 | [28 empty] | 130.681 | R U arm | 15 | 6
7 | Pelvis | 113.9238 | 0.60242 | 112.7 | 115.1 | [28 empty] | 152.4333 | L L arm | 12 | 7
8 | Head | 119.9619 | 0.35844 | 119.3 | 120.6 | [28 empty] | 134.0667 | R L arm | 13 | 8
9 | Top of head | 71.9619 | 0.3154 | 71.4 | 72.5 | [14 empty] | 14 | [5 empty] | 14 |  |  |  | 13 |  |  |  | 163.6762 | L hand | 10 | 9
10 | L. Hand | 163.6762 | 0.67 | 162.6 | 164.6 | [28 empty] | 187.3952 | R hand | 11 | 10
11 | R. Hand | 187.3952 | 0.35563 | 186.4 | 187.6 | [28 empty] | 101.0095 | L thigh | 5 | 11
12 | L. Forearm | 152.4333 | 1.0136 | 150.4 | 153.9 |  |  |  | y | [19 empty] | y |  |  |  |  | 105.319 | R thigh | 6 | 12
13 | R. Forearm | 134.0667 | 1.0758 | 132.4 | 135.6 | [14 empty] | 16 | [5 empty] | 16 |  |  |  | 15 |  |  |  | 144.2238 | L calf | 3 | 13
14 | L. Upper arm | 122.9095 | 0.37537 | 122.2 | 123.7 | [28 empty] | 145.5429 | R calf | 4 | 14
15 | R. Upper arm | 130.681 | 0.63688 | 129.7 | 132.1 |  |  |  | z |  |  | x | [13 empty] | z |  |  | x |  |  |  |  | 154.8476 | L foot | 1 | 15
16 | Chest | 117.7524 | 0.32499 | 117.2 | 118.6 | [28 empty] | 160.4238 | R foot | 2 | 16
17 | Back | 111.5048 | 0.65991 | 110.3 | 112.5 | [6 empty] | Corresponding zones on MANIKIN2 and 3 | [21 empty] | 111.5048 | Lo. back | 17 | 17
18 | All | 123.3 | 0.27568 | 122.8 | 123.9 | [28 empty] | 113.9238 | Seat | 7 | 18
| Temperatures: |  | Fluke Helios Plus 2287A with 40 Thermocouple Channels.
| Position |  | Temperatures (ºC) |  |  |  | Coordinates |  |  |  | 1325-1345
|  | ta [ºC] | STD [ºC] | Min | Max | x | y | z | [23 empty] | a | b | T=ax+b
1 | Vertical 1 | 19.6213 | 0.056484 | 19.5205 | 19.743 | -1.08 | 0.2 | 0.6 |  |  | 19.71 | 19.698 | 19.539 | 19.588 | 19.539 | 19.486 | 19.498 | 19.531 | 19.596 | 19.633 | 19.523 | 19.568 | 19.629 | 19.605 | 19.593 | 19.614 | 19.614 | 19.601 | 19.614 | 19.585 | 19.573 | 0.9933 | 0.1651 |  | 19.743 | 19.7311 | 19.5732 | 19.6219 | 19.5732 | 19.5205 | 19.5325 | 19.5652 | 19.6298 | 19.6666 | 19.5573 | 19.602 | 19.6626 | 19.6387 | 19.6268 | 19.6477 | 19.6477 | 19.6348 | 19.6477 | 19.6189 | 19.607
2 | Vertical 2 | 19.862 | 0.041826 | 19.7781 | 19.947 | -1.08 | 0.4 | 0.6 |  |  | 19.93 | 19.918 | 19.857 | 19.857 | 19.796 | 19.78 | 19.816 | 19.85 | 19.804 | 19.878 | 19.829 | 19.85 | 19.874 | 19.85 | 19.813 | 19.76 | 19.87 | 19.858 | 19.883 | 19.842 | 19.818 | 0.9932 | 0.1525 |  | 19.947 | 19.9351 | 19.8745 | 19.8745 | 19.8139 | 19.798 | 19.8338 | 19.8675 | 19.8218 | 19.8953 | 19.8467 | 19.8675 | 19.8914 | 19.8675 | 19.8308 | 19.7781 | 19.8874 | 19.8755 | 19.9003 | 19.8596 | 19.8357
3 | Vertical 3 | 20.0522 | 0.056829 | 19.9622 | 20.1722 | -1.08 | 0.6 | 0.6 |  |  | 20.184 | 20.184 | 20.062 | 20.123 | 20.099 | 20.046 | 19.997 | 20.116 | 19.973 | 20.083 | 20.046 | 20.091 | 20.091 | 20.018 | 20.067 | 20.014 | 20.063 | 20.027 | 20.039 | 19.998 | 20.011 | 0.9951 | 0.0871 |  | 20.1722 | 20.1722 | 20.0508 | 20.1115 | 20.0876 | 20.0349 | 19.9861 | 20.1045 | 19.9622 | 20.0717 | 20.0349 | 20.0797 | 20.0797 | 20.007 | 20.0558 | 20.003 | 20.0518 | 20.016 | 20.0279 | 19.9871 | 20
4 | Vertical 4 | 20.2734 | 0.090652 | 20.1356 | 20.4789 | -1.08 | 0.8 | 0.6 |  |  | 20.441 | 20.478 | 20.307 | 20.294 | 20.368 | 20.352 | 20.193 | 20.361 | 20.132 | 20.303 | 20.193 | 20.312 | 20.287 | 20.189 | 20.238 | 20.198 | 20.235 | 20.222 | 20.21 | 20.17 | 20.207 | 0.9922 | 0.1606 |  | 20.4422 | 20.4789 | 20.3092 | 20.2963 | 20.3697 | 20.3539 | 20.1961 | 20.3628 | 20.1356 | 20.3052 | 20.1961 | 20.3142 | 20.2894 | 20.1921 | 20.2407 | 20.2011 | 20.2378 | 20.2249 | 20.213 | 20.1733 | 20.21
5 | Vertical 5 | 20.4439 | 0.06869 | 20.3558 | 20.5871 | -1.08 | 1 | 0.6 |  |  | 20.671 | 20.695 | 20.609 | 20.585 | 20.622 | 20.643 | 20.508 | 20.59 | 20.508 | 20.582 | 20.487 | 20.566 | 20.566 | 20.483 | 20.517 | 20.479 | 20.538 | 20.513 | 20.501 | 20.464 | 20.464 | 1.0015 | -0.1389 |  | 20.5631 | 20.5871 | 20.501 | 20.477 | 20.514 | 20.5351 | 20.3999 | 20.482 | 20.3999 | 20.474 | 20.3788 | 20.4579 | 20.4579 | 20.3748 | 20.4089 | 20.3708 | 20.4299 | 20.4049 | 20.3929 | 20.3558 | 20.3558
6 | Vertical 6 | 20.5455 | 0.044511 | 20.4773 | 20.6254 | -1.08 | 1.2 | 0.6 |  |  | 20.695 | 20.695 | 20.683 | 20.658 | 20.658 | 20.643 | 20.582 | 20.614 | 20.606 | 20.643 | 20.582 | 20.614 | 20.627 | 20.566 | 20.59 | 20.562 | 20.611 | 20.574 | 20.587 | 20.571 | 20.546 | 0.994 | 0.0546 |  | 20.6254 | 20.6254 | 20.6135 | 20.5887 | 20.5887 | 20.5737 | 20.5131 | 20.5449 | 20.537 | 20.5737 | 20.5131 | 20.5449 | 20.5578 | 20.4972 | 20.5211 | 20.4932 | 20.5419 | 20.5052 | 20.5181 | 20.5022 | 20.4773
7 | Vertical 7 | 20.6304 | 0.034581 | 20.5779 | 20.694 | -1.08 | 1.4 | 0.6 |  |  | 20.732 | 20.72 | 20.732 | 20.744 | 20.695 | 20.716 | 20.655 | 20.651 | 20.692 | 20.692 | 20.679 | 20.676 | 20.688 | 20.627 | 20.663 | 20.684 | 20.672 | 20.648 | 20.648 | 20.632 | 20.632 | 0.9922 | 0.1118 |  | 20.6821 | 20.6702 | 20.6821 | 20.694 | 20.6454 | 20.6662 | 20.6057 | 20.6017 | 20.6424 | 20.6424 | 20.6295 | 20.6265 | 20.6384 | 20.5779 | 20.6136 | 20.6345 | 20.6226 | 20.5987 | 20.5987 | 20.5829 | 20.5829
8 | Vertical 8 | 20.6608 | 0.026534 | 20.6101 | 20.6952 | -1.08 | 1.6 | 0.6 |  |  | 20.818 | 20.805 | 20.818 | 20.818 | 20.793 | 20.79 | 20.777 | 20.749 | 20.802 | 20.802 | 20.814 | 20.786 | 20.798 | 20.774 | 20.786 | 20.782 | 20.77 | 20.746 | 20.733 | 20.754 | 20.742 | 1.0008 | -0.1395 |  | 20.6952 | 20.6821 | 20.6952 | 20.6952 | 20.6701 | 20.6671 | 20.6541 | 20.6261 | 20.6791 | 20.6791 | 20.6912 | 20.6631 | 20.6751 | 20.6511 | 20.6631 | 20.6591 | 20.6471 | 20.6231 | 20.6101 | 20.6311 | 20.6191
9 | Vertical 9 | 20.6626 | 0.025348 | 20.6114 | 20.6996 | -1.08 | 1.8 | 0.6 |  |  | 20.842 | 20.83 | 20.83 | 20.83 | 20.793 | 20.814 | 20.826 | 20.798 | 20.826 | 20.826 | 20.826 | 20.81 | 20.798 | 20.798 | 20.786 | 20.819 | 20.794 | 20.77 | 20.758 | 20.754 | 20.779 | 1.0022 | -0.1883 |  | 20.6996 | 20.6875 | 20.6875 | 20.6875 | 20.6504 | 20.6715 | 20.6835 | 20.6555 | 20.6835 | 20.6835 | 20.6835 | 20.6675 | 20.6555 | 20.6555 | 20.6434 | 20.6765 | 20.6514 | 20.6274 | 20.6154 | 20.6114 | 20.6364
10 | Vertical 10 | 20.6567 | 0.027083 | 20.5928 | 20.6927 | -1.08 | 2 | 0.6 |  |  | 20.854 | 20.854 | 20.854 | 20.842 | 20.818 | 20.826 | 20.851 | 20.823 | 20.839 | 20.826 | 20.826 | 20.823 | 20.798 | 20.81 | 20.798 | 20.819 | 20.807 | 20.782 | 20.794 | 20.754 | 20.779 | 0.9986 | -0.1321 |  | 20.6927 | 20.6927 | 20.6927 | 20.6807 | 20.6568 | 20.6647 | 20.6897 | 20.6617 | 20.6777 | 20.6647 | 20.6647 | 20.6617 | 20.6368 | 20.6488 | 20.6368 | 20.6578 | 20.6458 | 20.6208 | 20.6328 | 20.5928 | 20.6178
11 | Vertical 11 | 20.6643 | 0.029577 | 20.6101 | 20.7108 | -1.08 | 2.2 | 0.6 |  |  | 20.854 | 20.867 | 20.854 | 20.839 | 20.826 | 20.851 | 20.839 | 20.826 | 20.851 | 20.839 | 20.81 | 20.81 | 20.786 | 20.823 | 20.786 | 20.831 | 20.819 | 20.794 | 20.791 | 20.766 | 20.766 | 0.9974 | -0.1019 |  | 20.6979 | 20.7108 | 20.6979 | 20.6829 | 20.67 | 20.6949 | 20.6829 | 20.67 | 20.6949 | 20.6829 | 20.654 | 20.654 | 20.6301 | 20.667 | 20.6301 | 20.6749 | 20.663 | 20.638 | 20.635 | 20.6101 | 20.6101
12 | Vertical 12 | 20.6735 | 0.035731 | 20.6103 | 20.7315 | -1.08 | 2.4 | 0.6 |  |  | 20.891 | 20.891 | 20.903 | 20.875 | 20.875 | 20.912 | 20.875 | 20.863 | 20.887 | 20.875 | 20.823 | 20.81 | 20.798 | 20.859 | 20.823 | 20.868 | 20.843 | 20.831 | 20.828 | 20.815 | 20.791 | 1.0013 | -0.2077 |  | 20.7105 | 20.7105 | 20.7225 | 20.6944 | 20.6944 | 20.7315 | 20.6944 | 20.6824 | 20.7065 | 20.6944 | 20.6424 | 20.6294 | 20.6173 | 20.6784 | 20.6424 | 20.6874 | 20.6624 | 20.6504 | 20.6474 | 20.6344 | 20.6103
13 | Vertical 13 | 19.2674 | 0.067904 | 19.1316 | 19.3928 | 2.19 | 0.2 | 0.25 |  |  | 19.429 | 19.478 | 19.321 | 19.269 | 19.22 | 19.342 | 19.342 | 19.318 | 19.354 | 19.437 | 19.326 | 19.446 | 19.483 | 19.375 | 19.29 | 19.372 | 19.384 | 19.335 | 19.307 | 19.295 | 19.368 | 0.9932 | 0.0423 |  | 19.3392 | 19.3878 | 19.2319 | 19.1803 | 19.1316 | 19.2528 | 19.2528 | 19.2289 | 19.2647 | 19.3471 | 19.2369 | 19.3561 | 19.3928 | 19.2856 | 19.2011 | 19.2826 | 19.2945 | 19.2458 | 19.218 | 19.2061 | 19.2786
14 | Vertical 14 | 20.0974 | 0.052279 | 20.0289 | 20.1968 | 2.19 | 0.4 | 0.25 |  |  | 20.294 | 20.294 | 20.245 | 20.168 | 20.144 | 20.205 | 20.193 | 20.254 | 20.205 | 20.168 | 20.14 | 20.177 | 20.25 | 20.226 | 20.152 | 20.125 | 20.125 | 20.137 | 20.145 | 20.219 | 20.207 | 0.9934 | 0.0367 |  | 20.1968 | 20.1968 | 20.1481 | 20.0716 | 20.0477 | 20.1083 | 20.0964 | 20.157 | 20.1083 | 20.0716 | 20.0438 | 20.0805 | 20.1531 | 20.1292 | 20.0557 | 20.0289 | 20.0289 | 20.0408 | 20.0487 | 20.1223 | 20.1103
15 | Vertical 15 | 20.51 | 0.03054 | 20.47 | 20.578 | 2.19 | 0.6 | 0.25 |  |  | 20.695 | 20.707 | 20.671 | 20.667 | 20.655 | 20.667 | 20.63 | 20.667 | 20.618 | 20.643 | 20.627 | 20.614 | 20.651 | 20.614 | 20.627 | 20.611 | 20.623 | 20.599 | 20.607 | 20.62 | 20.607 | 0.9998 | -0.1249 |  | 20.566 | 20.578 | 20.542 | 20.538 | 20.526 | 20.538 | 20.501 | 20.538 | 20.489 | 20.514 | 20.498 | 20.485 | 20.522 | 20.485 | 20.498 | 20.482 | 20.494 | 20.47 | 20.478 | 20.491 | 20.478
16 | Vertical 16 | 20.6049 | 0.049217 | 20.5284 | 20.7127 | 2.19 | 0.8 | 0.25 |  |  | 20.756 | 20.781 | 20.707 | 20.692 | 20.716 | 20.716 | 20.679 | 20.679 | 20.679 | 20.716 | 20.627 | 20.663 | 20.688 | 20.602 | 20.639 | 20.66 | 20.66 | 20.623 | 20.595 | 20.632 | 20.607 | 0.9912 | 0.1146 |  | 20.6879 | 20.7127 | 20.6394 | 20.6245 | 20.6483 | 20.6483 | 20.6116 | 20.6116 | 20.6116 | 20.6483 | 20.5601 | 20.5958 | 20.6205 | 20.5353 | 20.572 | 20.5928 | 20.5928 | 20.5561 | 20.5284 | 20.565 | 20.5403
17 | Vertical 17 | 20.6946 | 0.042772 | 20.6298 | 20.7778 | 2.19 | 1 | 0.25 |  |  | 20.83 | 20.854 | 20.805 | 20.79 | 20.826 | 20.814 | 20.79 | 20.79 | 20.765 | 20.802 | 20.749 | 20.761 | 20.774 | 20.712 | 20.725 | 20.746 | 20.77 | 20.733 | 20.705 | 20.73 | 20.705 | 0.9928 | 0.0739 |  | 20.7539 | 20.7778 | 20.7291 | 20.7142 | 20.75 | 20.738 | 20.7142 | 20.7142 | 20.6894 | 20.7261 | 20.6735 | 20.6854 | 20.6983 | 20.6368 | 20.6497 | 20.6705 | 20.6944 | 20.6576 | 20.6298 | 20.6546 | 20.6298
18 | Vertical 18 | 20.7474 | 0.035092 | 20.6847 | 20.8082 | 2.19 | 1.2 | 0.25 |  |  | 20.903 | 20.903 | 20.879 | 20.851 | 20.875 | 20.875 | 20.851 | 20.863 | 20.839 | 20.875 | 20.835 | 20.835 | 20.847 | 20.81 | 20.81 | 20.819 | 20.831 | 20.807 | 20.791 | 20.803 | 20.779 | 0.996 | -0.0112 |  | 20.8082 | 20.8082 | 20.7843 | 20.7564 | 20.7803 | 20.7803 | 20.7564 | 20.7683 | 20.7444 | 20.7803 | 20.7405 | 20.7405 | 20.7524 | 20.7156 | 20.7156 | 20.7245 | 20.7365 | 20.7126 | 20.6966 | 20.7086 | 20.6847
19 | Vertical 19 | 20.6934 | 0.034624 | 20.6382 | 20.7503 | 2.19 | 1.4 | 0.25 |  |  | 20.818 | 20.83 | 20.805 | 20.79 | 20.802 | 20.814 | 20.79 | 20.777 | 20.777 | 20.814 | 20.761 | 20.761 | 20.774 | 20.725 | 20.725 | 20.77 | 20.77 | 20.758 | 20.717 | 20.73 | 20.717 | 0.9919 | 0.089 |  | 20.7384 | 20.7503 | 20.7255 | 20.7106 | 20.7225 | 20.7344 | 20.7106 | 20.6977 | 20.6977 | 20.7344 | 20.6818 | 20.6818 | 20.6947 | 20.6461 | 20.6461 | 20.6908 | 20.6908 | 20.6789 | 20.6382 | 20.6511 | 20.6382
20 | Vertical 20 | 20.7254 | 0.032311 | 20.6555 | 20.7754 | 2.19 | 1.6 | 0.25 |  |  | 20.854 | 20.867 | 20.854 | 20.826 | 20.875 | 20.863 | 20.839 | 20.826 | 20.839 | 20.863 | 20.798 | 20.81 | 20.835 | 20.786 | 20.798 | 20.819 | 20.831 | 20.807 | 20.791 | 20.779 | 20.754 | 0.9916 | 0.0758 |  | 20.7546 | 20.7675 | 20.7546 | 20.7269 | 20.7754 | 20.7636 | 20.7398 | 20.7269 | 20.7398 | 20.7636 | 20.6991 | 20.711 | 20.7358 | 20.6872 | 20.6991 | 20.7199 | 20.7318 | 20.708 | 20.6922 | 20.6803 | 20.6555
21 | Vertical 21 | 20.6027 | 0.021583 | 20.5553 | 20.6335 | 2.19 | 1.8 | 0.25 |  |  | 20.506 | 20.49 | 20.515 | 20.515 | 20.523 | 20.511 | 20.523 | 20.483 | 20.487 | 20.508 | 20.479 | 20.479 | 20.467 | 20.464 | 20.488 | 20.5 | 20.509 | 20.497 | 20.481 | 20.46 | 20.444 | 0.9907 | 0.3014 |  | 20.6167 | 20.6008 | 20.6256 | 20.6256 | 20.6335 | 20.6216 | 20.6335 | 20.5939 | 20.5979 | 20.6187 | 20.5899 | 20.5899 | 20.5781 | 20.5751 | 20.5989 | 20.6107 | 20.6197 | 20.6078 | 20.5919 | 20.5711 | 20.5553
22 | Vertical 22 | 20.6139 | 0.02219 | 20.5767 | 20.6556 | 2.19 | 2 | 0.25 |  |  | 20.592 | 20.588 | 20.613 | 20.588 | 20.609 | 20.597 | 20.621 | 20.581 | 20.584 | 20.581 | 20.565 | 20.553 | 20.553 | 20.561 | 20.574 | 20.598 | 20.582 | 20.582 | 20.554 | 20.546 | 20.542 | 0.9991 | 0.0532 |  | 20.6267 | 20.6227 | 20.6476 | 20.6227 | 20.6437 | 20.6317 | 20.6556 | 20.6157 | 20.6187 | 20.6157 | 20.5997 | 20.5877 | 20.5877 | 20.5957 | 20.6087 | 20.6327 | 20.6167 | 20.6167 | 20.5887 | 20.5807 | 20.5767
23 | Vertical 23 | 20.6137 | 0.026874 | 20.5605 | 20.6529 | 2.19 | 2.2 | 0.25 |  |  | 20.579 | 20.576 | 20.588 | 20.576 | 20.584 | 20.584 | 20.597 | 20.581 | 20.572 | 20.544 | 20.528 | 20.516 | 20.504 | 20.537 | 20.549 | 20.549 | 20.582 | 20.558 | 20.542 | 20.546 | 20.517 | 0.994 | 0.1795 |  | 20.635 | 20.632 | 20.644 | 20.632 | 20.64 | 20.64 | 20.6529 | 20.637 | 20.6281 | 20.6002 | 20.5843 | 20.5724 | 20.5605 | 20.5933 | 20.6052 | 20.6052 | 20.638 | 20.6142 | 20.5982 | 20.6022 | 20.5734
24 | Vertical 24 | 20.6102 | 0.02717 | 20.5645 | 20.6575 | 2.19 | 2.4 | 0.25 |  |  | 20.579 | 20.564 | 20.6 | 20.588 | 20.584 | 20.597 | 20.609 | 20.593 | 20.56 | 20.544 | 20.528 | 20.541 | 20.516 | 20.537 | 20.549 | 20.549 | 20.57 | 20.57 | 20.554 | 20.546 | 20.517 | 0.9999 | 0.0506 |  | 20.6275 | 20.6125 | 20.6485 | 20.6365 | 20.6325 | 20.6455 | 20.6575 | 20.6415 | 20.6085 | 20.5925 | 20.5765 | 20.5895 | 20.5645 | 20.5855 | 20.5975 | 20.5975 | 20.6185 | 20.6185 | 20.6025 | 20.5945 | 20.5655
25 | Air 0.1 | 19.2184 | 0.073804 | 19.0648 | 19.3384 | 1.22 | 0.1 | 1.1 |  |  | 19.071 | 19.019 | 19.113 | 19.08 | 19.064 | 18.966 | 18.978 | 19.118 | 19.101 | 19.167 | 18.946 | 19.127 | 19.152 | 19.099 | 19.148 | 19.221 | 19.108 | 19.181 | 19.104 | 19.144 | 19.202 | 0.9952 | 0.2097 |  | 19.1892 | 19.1374 | 19.231 | 19.1981 | 19.1822 | 19.0847 | 19.0966 | 19.2359 | 19.219 | 19.2847 | 19.0648 | 19.2449 | 19.2698 | 19.217 | 19.2658 | 19.3384 | 19.226 | 19.2986 | 19.222 | 19.2618 | 19.3195
26 | Air 0.6 | 20.1002 | 0.035484 | 20.0277 | 20.1848 | 1.22 | 0.6 | 1.1 |  |  | 20.056 | 20.053 | 20.065 | 20.04 | 20.037 | 20.037 | 20.049 | 20.119 | 20.025 | 20.009 | 20.017 | 20.03 | 20.079 | 20.038 | 20.051 | 20.014 | 19.961 | 19.961 | 19.994 | 20.047 | 20.031 | 0.994 | 0.1865 |  | 20.1222 | 20.1192 | 20.1311 | 20.1063 | 20.1033 | 20.1033 | 20.1152 | 20.1848 | 20.0913 | 20.0754 | 20.0834 | 20.0963 | 20.145 | 20.1043 | 20.1172 | 20.0804 | 20.0277 | 20.0277 | 20.0605 | 20.1132 | 20.0973
27 | Air 1.1 | 20.5721 | 0.049868 | 20.4963 | 20.6567 | 1.22 | 1.1 | 1.1 |  |  | 20.579 | 20.6 | 20.564 | 20.576 | 20.572 | 20.572 | 20.523 | 20.532 | 20.523 | 20.544 | 20.492 | 20.504 | 20.516 | 20.439 | 20.476 | 20.5 | 20.497 | 20.448 | 20.444 | 20.472 | 20.444 | 0.9962 | 0.135 |  | 20.6358 | 20.6567 | 20.6209 | 20.6328 | 20.6288 | 20.6288 | 20.58 | 20.589 | 20.58 | 20.6009 | 20.5491 | 20.5611 | 20.573 | 20.4963 | 20.5332 | 20.5571 | 20.5541 | 20.5053 | 20.5013 | 20.5292 | 20.5013
28 | Air 1.5 | 20.6805 | 0.040504 | 20.5897 | 20.7417 | 1.22 | 1.5 | 1.1 |  |  | 20.653 | 20.649 | 20.649 | 20.625 | 20.67 | 20.658 | 20.633 | 20.618 | 20.646 | 20.63 | 20.602 | 20.577 | 20.565 | 20.574 | 20.586 | 20.598 | 20.619 | 20.595 | 20.554 | 20.558 | 20.517 | 0.9935 | 0.2061 |  | 20.7249 | 20.7209 | 20.7209 | 20.697 | 20.7417 | 20.7298 | 20.705 | 20.6901 | 20.7179 | 20.702 | 20.6742 | 20.6493 | 20.6374 | 20.6464 | 20.6583 | 20.6702 | 20.6911 | 20.6672 | 20.6265 | 20.6305 | 20.5897
29 | Cieling | 20.6722 | 0.032876 | 20.6137 | 20.718 | 0 | 2.46 | 0.6 |  |  | 20.665 | 20.662 | 20.674 | 20.662 | 20.682 | 20.67 | 20.67 | 20.679 | 20.646 | 20.618 | 20.59 | 20.602 | 20.577 | 20.61 | 20.623 | 20.623 | 20.644 | 20.631 | 20.615 | 20.631 | 20.579 | 0.9933 | 0.1746 |  | 20.7011 | 20.6982 | 20.7101 | 20.6982 | 20.718 | 20.7061 | 20.7061 | 20.7151 | 20.6823 | 20.6545 | 20.6266 | 20.6386 | 20.6137 | 20.6465 | 20.6594 | 20.6594 | 20.6803 | 20.6674 | 20.6515 | 20.6674 | 20.6157
30 | Floor | 20.8266 | 0.013818 | 20.7978 | 20.8593 | 1.85 | 0 | 0.6 |  |  | 20.812 | 20.796 | 20.796 | 20.784 | 20.78 | 20.793 | 20.793 | 20.777 | 20.78 | 20.777 | 20.773 | 20.785 | 20.773 | 20.782 | 20.769 | 20.769 | 20.778 | 20.766 | 20.762 | 20.766 | 20.75 | 0.9921 | 0.2117 |  | 20.8593 | 20.8434 | 20.8434 | 20.8315 | 20.8275 | 20.8404 | 20.8404 | 20.8246 | 20.8275 | 20.8246 | 20.8206 | 20.8325 | 20.8206 | 20.8295 | 20.8166 | 20.8166 | 20.8256 | 20.8136 | 20.8097 | 20.8136 | 20.7978
31 | Floor | 24.2981 | 0.022671 | 24.2688 | 24.3456 | 0.59 | 0 | 0.6 |  |  | 24.276 | 24.288 | 24.285 | 24.24 | 24.245 | 24.245 | 24.249 | 24.254 | 24.242 | 24.266 | 24.229 | 24.229 | 24.229 | 24.214 | 24.214 | 24.226 | 24.226 | 24.21 | 24.231 | 24.219 | 24.219 | 0.9847 | 0.4292 |  | 24.3338 | 24.3456 | 24.3426 | 24.2983 | 24.3033 | 24.3033 | 24.3072 | 24.3121 | 24.3003 | 24.3239 | 24.2875 | 24.2875 | 24.2875 | 24.2727 | 24.2727 | 24.2845 | 24.2845 | 24.2688 | 24.2895 | 24.2776 | 24.2776
32 | Floor | 19.7937 | 0.038797 | 19.7384 | 19.8906 | 0 | 0 | 0.6 |  |  | 19.824 | 19.824 | 19.747 | 19.734 | 19.719 | 19.731 | 19.734 | 19.703 | 19.691 | 19.739 | 19.699 | 19.724 | 19.699 | 19.683 | 19.671 | 19.732 | 19.745 | 19.741 | 19.717 | 19.713 | 19.688 | 0.9948 | 0.1697 |  | 19.8906 | 19.8906 | 19.814 | 19.8011 | 19.7862 | 19.7981 | 19.8011 | 19.7702 | 19.7583 | 19.8061 | 19.7663 | 19.7911 | 19.7663 | 19.7503 | 19.7384 | 19.7991 | 19.812 | 19.808 | 19.7842 | 19.7802 | 19.7553
33 | Mid cieling | 20.8034 | 0.021089 | 20.7763 | 20.8381 | 1.22 | 2.46 | 0.6 |  |  | 20.775 | 20.775 | 20.759 | 20.759 | 20.768 | 20.756 | 20.759 | 20.752 | 20.74 | 20.74 | 20.736 | 20.749 | 20.736 | 20.72 | 20.72 | 20.72 | 20.72 | 20.717 | 20.717 | 20.713 | 20.713 | 0.9972 | 0.1213 |  | 20.8381 | 20.8381 | 20.8222 | 20.8222 | 20.8311 | 20.8192 | 20.8222 | 20.8152 | 20.8032 | 20.8032 | 20.7992 | 20.8122 | 20.7992 | 20.7833 | 20.7833 | 20.7833 | 20.7833 | 20.7803 | 20.7803 | 20.7763 | 20.7763
34 | Window wall | 20.9939 | 0.021992 | 20.9585 | 21.0322 | 0.59 | 1.23 | 1.2 |  |  | 20.956 | 20.944 | 20.94 | 20.94 | 20.936 | 20.936 | 20.94 | 20.921 | 20.921 | 20.933 | 20.917 | 20.917 | 20.917 | 20.901 | 20.901 | 20.901 | 20.901 | 20.885 | 20.897 | 20.882 | 20.882 | 0.9966 | 0.1475 |  | 21.0322 | 21.0203 | 21.0163 | 21.0163 | 21.0123 | 21.0123 | 21.0163 | 20.9974 | 20.9974 | 21.0093 | 20.9934 | 20.9934 | 20.9934 | 20.9774 | 20.9774 | 20.9774 | 20.9774 | 20.9615 | 20.9735 | 20.9585 | 20.9585
35 | Window wall | 20.9477 | 0.019412 | 20.9159 | 20.9866 | 1.85 | 1.23 | 1.2 |  |  | 20.907 | 20.895 | 20.891 | 20.879 | 20.887 | 20.875 | 20.891 | 20.872 | 20.859 | 20.872 | 20.868 | 20.88 | 20.868 | 20.852 | 20.852 | 20.852 | 20.852 | 20.836 | 20.848 | 20.845 | 20.845 | 0.9957 | 0.1695 |  | 20.9866 | 20.9747 | 20.9707 | 20.9587 | 20.9667 | 20.9547 | 20.9707 | 20.9518 | 20.9388 | 20.9518 | 20.9478 | 20.9597 | 20.9478 | 20.9318 | 20.9318 | 20.9318 | 20.9318 | 20.9159 | 20.9279 | 20.9249 | 20.9249
36 | Door wall | 20.3779 | 0.023341 | 20.3339 | 20.4172 | 1.85 | 1.23 | 0 |  |  | 20.286 | 20.286 | 20.27 | 20.27 | 20.266 | 20.266 | 20.27 | 20.25 | 20.241 | 20.25 | 20.247 | 20.247 | 20.247 | 20.234 | 20.234 | 20.222 | 20.222 | 20.218 | 20.218 | 20.227 | 20.202 | 0.9912 | 0.3097 |  | 20.4172 | 20.4172 | 20.4013 | 20.4013 | 20.3974 | 20.3974 | 20.4013 | 20.3815 | 20.3726 | 20.3815 | 20.3785 | 20.3785 | 20.3785 | 20.3656 | 20.3656 | 20.3537 | 20.3537 | 20.3498 | 20.3498 | 20.3587 | 20.3339
37 | Door wall | 20.4656 | 0.027307 | 20.4319 | 20.5164 | 0.59 | 1.23 | 0 |  |  | 20.335 | 20.347 | 20.331 | 20.331 | 20.315 | 20.328 | 20.319 | 20.299 | 20.287 | 20.299 | 20.284 | 20.296 | 20.284 | 20.28 | 20.268 | 20.28 | 20.268 | 20.264 | 20.264 | 20.261 | 20.261 | 0.9828 | 0.5194 |  | 20.5046 | 20.5164 | 20.5007 | 20.5007 | 20.485 | 20.4978 | 20.4889 | 20.4693 | 20.4575 | 20.4693 | 20.4545 | 20.4663 | 20.4545 | 20.4506 | 20.4388 | 20.4506 | 20.4388 | 20.4349 | 20.4349 | 20.4319 | 20.4319
38 | Upper outlet | 20.722 | 0.05083 | 20.635 | 20.8021 | 2.44 | 1.84 | 0.6 |  |  | 20.641 | 20.641 | 20.637 | 20.625 | 20.682 | 20.67 | 20.637 | 20.605 | 20.642 | 20.605 | 20.553 | 20.541 | 20.516 | 20.684 | 20.561 | 20.635 | 20.574 | 20.582 | 20.558 | 20.554 | 20.53 | 0.9946 | 0.2298 |  | 20.7593 | 20.7593 | 20.7554 | 20.7434 | 20.8001 | 20.7882 | 20.7554 | 20.7235 | 20.7603 | 20.7235 | 20.6718 | 20.6599 | 20.635 | 20.8021 | 20.6798 | 20.7534 | 20.6927 | 20.7007 | 20.6768 | 20.6728 | 20.6489
39 | Lower outlet | 20.267 | 0.08169 | 20.1475 | 20.4785 | 2.44 | 0.63 | 0.6 |  |  | 20.347 | 20.142 | 20.077 | 20.151 | 20.22 | 20.254 | 20.126 | 20.205 | 20.107 | 20.033 | 20.079 | 20.115 | 20.201 | 20.087 | 20.148 | 20.148 | 20.014 | 20.059 | 20.096 | 20.19 | 20.019 | 0.9939 | 0.2556 |  | 20.4785 | 20.2747 | 20.2101 | 20.2837 | 20.3523 | 20.3861 | 20.2588 | 20.3373 | 20.2399 | 20.1664 | 20.2121 | 20.2479 | 20.3334 | 20.2201 | 20.2807 | 20.2807 | 20.1475 | 20.1922 | 20.229 | 20.3224 | 20.1525
40 | Back wall | 20.9107 | 0.027018 | 20.871 | 20.9628 | 2.44 | 1.23 | 0.6 |  |  | 20.846 | 20.858 | 20.83 | 20.83 | 20.839 | 20.826 | 20.83 | 20.813 | 20.801 | 20.813 | 20.798 | 20.819 | 20.798 | 20.782 | 20.782 | 20.782 | 20.782 | 20.766 | 20.778 | 20.774 | 20.774 | 0.9974 | 0.159 |  | 20.9508 | 20.9628 | 20.9348 | 20.9348 | 20.9438 | 20.9309 | 20.9348 | 20.9179 | 20.9059 | 20.9179 | 20.9029 | 20.9239 | 20.9029 | 20.887 | 20.887 | 20.887 | 20.887 | 20.871 | 20.883 | 20.879 | 20.879
| Air velocities: |  | Dantec Dynamics Indoor Flow System with 5 54T21 Omnidirectional Transducers.
| Position |  | Air velocities (m/s) |  |  |  | Coordinates |  |  |  | 151.6 | 157.9 | 153 | 152.8 | 151 | 154.8 | 157.6 | 152.8 | 153.5 | 154.7 | 156 | 155.8 | 156 | 156.1 | 154.3 | 151.3 | 152.8 | 157.4 | 155.6 | 158.2 | 158.6 |  | L. Foot |  | 154.8476 | 2.3505 | 151 | 158.6
|  | va [m/s] | STD [m/s] | Tu % |  | x | y | z |  |  | 158.6 | 163 | 161.4 | 160.2 | 159.3 | 161.5 | 161 | 159.3 | 156.8 | 162.9 | 160.2 | 160 | 162.6 | 160 | 159.3 | 157 | 160.1 | 162.1 | 160.4 | 161.6 | 161.6 |  | R. Foot |  | 160.4238 | 1.7038 | 156.8 | 163
1 | Air vel. 1 | 0.292 | 0.017 | 5.93 |  | 0.19 | 1.3 | 0 |  |  | 143.4 | 144.4 | 144 | 144.2 | 144.1 | 143.7 | 144.8 | 144.5 | 143.8 | 144.5 | 144.6 | 144.2 | 144.1 | 144.1 | 144.2 | 143.2 | 145 | 145 | 144.1 | 144.8 | 144 |  | L. Low leg |  | 144.2238 | 0.47635 | 143.2 | 145
2 | Air vel. 2 | 0.269 | 0.014 | 5.195 |  | 0.19 | 1.1 | 0 |  |  | 143.8 | 145.8 | 144.4 | 144.1 | 144.4 | 144.6 | 147.2 | 144.6 | 145.5 | 145.4 | 146.2 | 145.7 | 146.5 | 146.7 | 145.7 | 144.1 | 145.1 | 147 | 146.1 | 146.8 | 146.7 |  | R. Low leg |  | 145.5429 | 1.0656 | 143.8 | 147.2
3 | Air vel. 3 | 0.254 | 0.01 | 3.815 |  | 0.19 | 0.875 | 0 |  |  | 101.1 | 101.6 | 100.8 | 101.4 | 100.3 | 100.6 | 101.3 | 101.2 | 100.7 | 100.7 | 101.1 | 100.7 | 101 | 101.1 | 100.8 | 100.7 | 101.1 | 101.2 | 100.9 | 101.2 | 101.7 |  | L. Thigh |  | 101.0095 | 0.34337 | 100.3 | 101.7
4 | Air vel. 4 | 0.243 | 0.009 | 3.551 |  | 0.19 | 0.55 | 0 |  |  | 104.9 | 105.1 | 105.5 | 105.6 | 105.4 | 105.7 | 105.8 | 105.2 | 105 | 105.4 | 105.1 | 104.8 | 105.1 | 104.8 | 105.6 | 105.1 | 105.6 | 105.1 | 105.4 | 105.7 | 105.8 |  | R. Thigh |  | 105.319 | 0.32499 | 104.8 | 105.8
5 | Air vel. 5 | 0.278 | 0.036 | 12.962 |  | 0.19 | 0.275 | 0 |  |  | 114 | 112.7 | 113.7 | 113 | 113.9 | 113.2 | 113.2 | 114 | 114.5 | 113.7 | 114.4 | 113.9 | 114.1 | 114.1 | 114.9 | 114.1 | 115.1 | 113.6 | 113.7 | 114.7 | 113.9 |  | Pelvis |  | 113.9238 | 0.60242 | 112.7 | 115.1
6 | Air vel. 6 | 0.186 | 0.077 | 41.344 |  | 2.19 | 1.3 | 0 |  |  | 119.7 | 120.1 | 119.3 | 119.8 | 119.3 | 119.9 | 119.7 | 119.9 | 120.4 | 119.9 | 120.1 | 119.7 | 119.8 | 120 | 120.3 | 119.8 | 120.4 | 120.6 | 119.8 | 120.6 | 120.1 |  | Head |  | 119.9619 | 0.35844 | 119.3 | 120.6
7 | Air vel. 7 | 0.228 | 0.057 | 24.867 |  | 2.19 | 1.1 | 0 |  |  | 71.4 | 71.5 | 71.4 | 71.7 | 71.7 | 71.8 | 71.6 | 72 | 72 | 72.1 | 72.1 | 72.1 | 72 | 72.1 | 72.2 | 71.9 | 72.3 | 72.5 | 72.2 | 72.4 | 72.2 |  | Top of head |  | 71.9619 | 0.3154 | 71.4 | 72.5
8 | Air vel. 8 | 0.72 | 0.053 | 7.357 |  | 2.19 | 0.875 | 0 |  |  | 162.6 | 163.9 | 163.3 | 163.3 | 163.4 | 164.3 | 164.5 | 164.3 | 164.1 | 164 | 162.9 | 162.8 | 164 | 162.7 | 164.1 | 164.6 | 163.1 | 164.3 | 162.9 | 163.5 | 164.6 |  | L. Hand |  | 163.6762 | 0.67 | 162.6 | 164.6
9 | Air vel. 9 | 0.982 | 0.043 | 4.383 |  | 2.19 | 0.55 | 0 |  |  | 187.5 | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.2 | 187.6 | 187.6 | 187.4 | 186.6 | 186.8 | 186.4 | 187.5 | 187.5 | 187.6 | 187.6 | 187.3 | 187.5 | 187.6 |  | R. Hand |  | 187.3952 | 0.35563 | 186.4 | 187.6
10 | Air vel. 10 | 0.469 | 0.032 | 6.849 |  | 2.19 | 0.275 | 0 |  |  | 150.4 | 153.4 | 152.3 | 151.7 | 151.3 | 153.8 | 153.3 | 153.9 | 151.1 | 152.9 | 151.4 | 152.2 | 152.9 | 152.3 | 152.6 | 151.9 | 150.9 | 153.5 | 152.8 | 152.9 | 153.6 |  | L. Forearm |  | 152.4333 | 1.0136 | 150.4 | 153.9
[11 empty] | 134.9 | 133 | 134.3 | 135.4 | 135.4 | 133.6 | 133.3 | 135.1 | 135.6 | 133.2 | 134 | 132.9 | 133 | 133.1 | 134.9 | 135.2 | 135.6 | 132.4 | 132.6 | 134 | 133.9 |  | R. Forearm |  | 134.0667 | 1.0758 | 132.4 | 135.6
[11 empty] | 122.8 | 123.1 | 122.5 | 122.8 | 122.2 | 122.4 | 122.4 | 122.9 | 123 | 123.1 | 123.3 | 122.8 | 123.3 | 122.9 | 123 | 123.1 | 123.2 | 123.4 | 122.7 | 123.7 | 122.5 |  | L. Upper arm |  | 122.9095 | 0.37537 | 122.2 | 123.7
[11 empty] | 131.4 | 130.3 | 130.3 | 130.7 | 130 | 130.4 | 129.9 | 132.1 | 131.6 | 130.9 | 131 | 129.7 | 130.4 | 130 | 131 | 131.2 | 131.6 | 130.7 | 130.1 | 130.6 | 130.4 |  | R. Upper arm |  | 130.681 | 0.63688 | 129.7 | 132.1
[11 empty] | 117.9 | 118.1 | 117.4 | 117.2 | 117.3 | 117.8 | 117.6 | 117.5 | 117.9 | 118 | 117.6 | 117.7 | 117.7 | 117.4 | 117.6 | 117.8 | 118.6 | 118.2 | 117.8 | 117.7 | 118 |  | Chest |  | 117.7524 | 0.32499 | 117.2 | 118.6
[11 empty] | 111.7 | 110.7 | 110.5 | 111 | 111.2 | 110.6 | 110.3 | 112.2 | 112.5 | 111.6 | 112.2 | 111.5 | 111.6 | 111.1 | 111.3 | 112.5 | 111.9 | 111.4 | 111.4 | 112.4 | 112 |  | Back |  | 111.5048 | 0.65991 | 110.3 | 112.5
[11 empty] | 122.9 | 123.3 | 123 | 123 | 122.8 | 123.1 | 123.4 | 123.4 | 123.3 | 123.4 | 123.5 | 123.1 | 123.4 | 123.2 | 123.4 | 123.1 | 123.6 | 123.6 | 123.2 | 123.9 | 123.7 |  | All |  | 123.3 | 0.27568 | 122.8 | 123.9

## HL4@va0.27ta20
Manikin heat loss in windtunnel
| Nom. Inlet velocity |  | 0.2 | m/s | Nom. Air temperature |  | 20 | ºC
| Mean Inlet velocity |  | 0.2672 | m/s | Mean Air temp. |  | 20.337 | ºC
[10 empty] | 1 |  | 2 | [15 empty] | 2
| Std. dev. Inlet vel. |  | 0.0172 | m/s | Std. dev. Air temp. |  | 0.0417 | ºC
1
| Mean Inlet Turb. intens. |  | 6.2906 | % | Mean Wall temp. |  | 20.9477 | ºC
| Relative Humidity |  | 35 | % | Air Pressure |  | 1027.15 | mbar | 4 |  |  | 3 | [12 empty] | 6 | [6 empty] | 5
| Thermal manikin: |  | Comfortina, No clothing, Software version 3.0.30. | [6 empty] | 6 | [17 empty] | 3
| Body Segments |  | Heat loss (W/m2) | [30 empty] | H L (W/m2) | Zones | No
|  | Q [W/m2] | STD [W/m2] | Min | Max | [7 empty] | 8 |  |  |  | 10 | [7 empty] | 10 | [6 empty] | 11 |  | 123.8286 | Total | 18
1 | L. Foot | 154.1238 | 1.8839 | 151 | 157.5 | [28 empty] | 72.2905 | Scalp | 9 | 1
2 | R. Foot | 160.7952 | 1.7854 | 157.3 | 164.2 |  |  |  |  | 17 | [23 empty] | 120.5238 | Face | 8 | 2
3 | L. Low leg | 144.8381 | 0.33537 | 144.1 | 145.3 | [28 empty] | 118.3952 | Chest | 16 | 3
4 | R. Low leg | 145.8857 | 0.6923 | 144.6 | 147 | [5 empty] | 18 |  |  |  |  | 12 | [9 empty] | 12 |  | 18 |  | 11 |  |  |  | 112.5857 | Up. back | 17 | 4
5 | L. Thigh | 101.2476 | 0.47183 | 100.4 | 102.4 | [28 empty] | 123.6429 | L U arm | 14 | 5
6 | R. Thigh | 105.4952 | 0.50742 | 104.5 | 106.5 | [28 empty] | 131.4143 | R U arm | 15 | 6
7 | Pelvis | 114.7 | 0.39875 | 114 | 115.6 | [28 empty] | 152.9429 | L L arm | 12 | 7
8 | Head | 120.5238 | 0.40976 | 119.7 | 121.1 | [28 empty] | 135.0905 | R L arm | 13 | 8
9 | Top of head | 72.2905 | 0.3375 | 71.8 | 73 | [14 empty] | 14 | [5 empty] | 14 |  |  |  | 13 |  |  |  | 164.419 | L hand | 10 | 9
10 | L. Hand | 164.419 | 0.87728 | 163.2 | 166.1 | [28 empty] | 187.5095 | R hand | 11 | 10
11 | R. Hand | 187.5095 | 0.26628 | 186.4 | 187.6 | [28 empty] | 101.2476 | L thigh | 5 | 11
12 | L. Forearm | 152.9429 | 1.3822 | 149.9 | 156 |  |  |  | y | [19 empty] | y |  |  |  |  | 105.4952 | R thigh | 6 | 12
13 | R. Forearm | 135.0905 | 1.4237 | 131.2 | 137.6 | [14 empty] | 16 | [5 empty] | 16 |  |  |  | 15 |  |  |  | 144.8381 | L calf | 3 | 13
14 | L. Upper arm | 123.6429 | 0.79093 | 122 | 125.1 | [28 empty] | 145.8857 | R calf | 4 | 14
15 | R. Upper arm | 131.4143 | 0.73572 | 130.1 | 132.8 |  |  |  | z |  |  | x | [13 empty] | z |  |  | x |  |  |  |  | 154.1238 | L foot | 1 | 15
16 | Chest | 118.3952 | 0.33686 | 117.9 | 119 | [28 empty] | 160.7952 | R foot | 2 | 16
17 | Back | 112.5857 | 0.95671 | 110.1 | 114.2 | [6 empty] | Corresponding zones on MANIKIN2 and 3 | [21 empty] | 112.5857 | Lo. back | 17 | 17
18 | All | 123.8286 | 0.30519 | 123.3 | 124.5 | [28 empty] | 114.7 | Seat | 7 | 18
| Temperatures: |  | Fluke Helios Plus 2287A with 40 Thermocouple Channels.
| Position |  | Temperatures (ºC) |  |  |  | Coordinates |  |  |  | 1440-1460
|  | ta [ºC] | STD [ºC] | Min | Max | x | y | z | [23 empty] | a | b | T=ax+b
1 | Vertical 1 | 19.5694 | 0.040064 | 19.4788 | 19.6457 | -1.08 | 0.2 | 0.6 |  |  | 19.549 | 19.537 | 19.5 | 19.488 | 19.549 | 19.5 | 19.513 | 19.574 | 19.57 | 19.558 | 19.546 | 19.534 | 19.607 | 19.518 | 19.444 | 19.481 | 19.542 | 19.514 | 19.551 | 19.551 | 19.612 | 0.9933 | 0.1651 |  | 19.5831 | 19.5712 | 19.5344 | 19.5225 | 19.5831 | 19.5344 | 19.5474 | 19.608 | 19.604 | 19.5921 | 19.5801 | 19.5682 | 19.6407 | 19.5523 | 19.4788 | 19.5156 | 19.5762 | 19.5484 | 19.5851 | 19.5851 | 19.6457
2 | Vertical 2 | 19.8008 | 0.037172 | 19.7076 | 19.8606 | -1.08 | 0.4 | 0.6 |  |  | 19.843 | 19.831 | 19.843 | 19.77 | 19.794 | 19.77 | 19.806 | 19.806 | 19.815 | 19.778 | 19.766 | 19.778 | 19.815 | 19.75 | 19.726 | 19.689 | 19.763 | 19.771 | 19.796 | 19.759 | 19.771 | 0.9932 | 0.1525 |  | 19.8606 | 19.8486 | 19.8606 | 19.7881 | 19.8119 | 19.7881 | 19.8238 | 19.8238 | 19.8328 | 19.796 | 19.7841 | 19.796 | 19.8328 | 19.7682 | 19.7444 | 19.7076 | 19.7811 | 19.7891 | 19.8139 | 19.7771 | 19.7891
3 | Vertical 3 | 19.9864 | 0.063219 | 19.8498 | 20.0976 | -1.08 | 0.6 | 0.6 |  |  | 20.073 | 20.109 | 20.097 | 19.975 | 20.024 | 20.048 | 20.011 | 20.048 | 20.069 | 19.983 | 19.934 | 19.971 | 19.983 | 19.931 | 19.906 | 19.86 | 19.967 | 19.976 | 20.025 | 20.001 | 19.952 | 0.9951 | 0.0871 |  | 20.0617 | 20.0976 | 20.0856 | 19.9642 | 20.013 | 20.0369 | 20 | 20.0369 | 20.0578 | 19.9722 | 19.9234 | 19.9602 | 19.9722 | 19.9204 | 19.8956 | 19.8498 | 19.9563 | 19.9652 | 20.014 | 19.9901 | 19.9413
4 | Vertical 4 | 20.2043 | 0.085651 | 20.0542 | 20.3578 | -1.08 | 0.8 | 0.6 |  |  | 20.171 | 20.244 | 20.232 | 20.085 | 20.232 | 20.317 | 20.207 | 20.305 | 20.277 | 20.24 | 20.204 | 20.155 | 20.142 | 20.102 | 20.09 | 20.078 | 20.225 | 20.294 | 20.356 | 20.221 | 20.05 | 0.9922 | 0.1606 |  | 20.1743 | 20.2467 | 20.2348 | 20.0889 | 20.2348 | 20.3191 | 20.21 | 20.3072 | 20.2794 | 20.2427 | 20.207 | 20.1584 | 20.1455 | 20.1058 | 20.0939 | 20.082 | 20.2278 | 20.2963 | 20.3578 | 20.2239 | 20.0542
5 | Vertical 5 | 20.3933 | 0.053632 | 20.2717 | 20.476 | -1.08 | 1 | 0.6 |  |  | 20.449 | 20.498 | 20.473 | 20.403 | 20.522 | 20.584 | 20.486 | 20.535 | 20.519 | 20.58 | 20.543 | 20.543 | 20.47 | 20.454 | 20.454 | 20.491 | 20.527 | 20.548 | 20.536 | 20.536 | 20.38 | 1.0015 | -0.1389 |  | 20.3408 | 20.3898 | 20.3648 | 20.2947 | 20.4139 | 20.476 | 20.3778 | 20.4269 | 20.4109 | 20.472 | 20.4349 | 20.4349 | 20.3618 | 20.3458 | 20.3458 | 20.3828 | 20.4189 | 20.4399 | 20.4279 | 20.4279 | 20.2717
6 | Vertical 6 | 20.4831 | 0.043412 | 20.3948 | 20.5598 | -1.08 | 1.2 | 0.6 |  |  | 20.498 | 20.522 | 20.522 | 20.486 | 20.547 | 20.608 | 20.522 | 20.547 | 20.555 | 20.604 | 20.629 | 20.629 | 20.58 | 20.54 | 20.527 | 20.552 | 20.552 | 20.573 | 20.573 | 20.56 | 20.463 | 0.994 | 0.0546 |  | 20.4296 | 20.4535 | 20.4535 | 20.4177 | 20.4783 | 20.539 | 20.4535 | 20.4783 | 20.4863 | 20.535 | 20.5598 | 20.5598 | 20.5111 | 20.4714 | 20.4584 | 20.4833 | 20.4833 | 20.5042 | 20.5042 | 20.4912 | 20.3948
7 | Vertical 7 | 20.5722 | 0.030459 | 20.5114 | 20.6285 | -1.08 | 1.4 | 0.6 |  |  | 20.596 | 20.62 | 20.657 | 20.62 | 20.633 | 20.645 | 20.584 | 20.584 | 20.617 | 20.653 | 20.666 | 20.678 | 20.666 | 20.625 | 20.613 | 20.613 | 20.601 | 20.597 | 20.609 | 20.609 | 20.56 | 0.9922 | 0.1118 |  | 20.5472 | 20.571 | 20.6077 | 20.571 | 20.5839 | 20.5958 | 20.5352 | 20.5352 | 20.568 | 20.6037 | 20.6166 | 20.6285 | 20.6166 | 20.5759 | 20.564 | 20.564 | 20.5521 | 20.5481 | 20.56 | 20.56 | 20.5114
8 | Vertical 8 | 20.5945 | 0.025691 | 20.559 | 20.6411 | -1.08 | 1.6 | 0.6 |  |  | 20.718 | 20.718 | 20.743 | 20.743 | 20.73 | 20.743 | 20.694 | 20.682 | 20.702 | 20.739 | 20.751 | 20.764 | 20.751 | 20.723 | 20.687 | 20.699 | 20.687 | 20.707 | 20.683 | 20.707 | 20.695 | 1.0008 | -0.1395 |  | 20.5951 | 20.5951 | 20.6201 | 20.6201 | 20.6071 | 20.6201 | 20.5711 | 20.559 | 20.5791 | 20.6161 | 20.6281 | 20.6411 | 20.6281 | 20.6001 | 20.564 | 20.5761 | 20.564 | 20.5841 | 20.56 | 20.5841 | 20.5721
9 | Vertical 9 | 20.6028 | 0.03023 | 20.5442 | 20.6615 | -1.08 | 1.8 | 0.6 |  |  | 20.779 | 20.743 | 20.804 | 20.779 | 20.755 | 20.767 | 20.755 | 20.73 | 20.727 | 20.764 | 20.764 | 20.776 | 20.764 | 20.748 | 20.723 | 20.711 | 20.687 | 20.695 | 20.707 | 20.732 | 20.744 | 1.0022 | -0.1883 |  | 20.6364 | 20.6003 | 20.6615 | 20.6364 | 20.6124 | 20.6244 | 20.6124 | 20.5873 | 20.5843 | 20.6214 | 20.6214 | 20.6334 | 20.6214 | 20.6053 | 20.5803 | 20.5683 | 20.5442 | 20.5522 | 20.5643 | 20.5893 | 20.6013
10 | Vertical 10 | 20.6006 | 0.029849 | 20.5499 | 20.6667 | -1.08 | 2 | 0.6 |  |  | 20.804 | 20.779 | 20.828 | 20.792 | 20.767 | 20.792 | 20.779 | 20.743 | 20.739 | 20.751 | 20.776 | 20.788 | 20.776 | 20.76 | 20.736 | 20.736 | 20.711 | 20.732 | 20.72 | 20.744 | 20.744 | 0.9986 | -0.1321 |  | 20.6428 | 20.6178 | 20.6667 | 20.6308 | 20.6058 | 20.6308 | 20.6178 | 20.5819 | 20.5779 | 20.5898 | 20.6148 | 20.6268 | 20.6148 | 20.5988 | 20.5749 | 20.5749 | 20.5499 | 20.5709 | 20.5589 | 20.5829 | 20.5829
11 | Vertical 11 | 20.6141 | 0.03012 | 20.5672 | 20.6759 | -1.08 | 2.2 | 0.6 |  |  | 20.832 | 20.779 | 20.828 | 20.779 | 20.767 | 20.792 | 20.804 | 20.751 | 20.751 | 20.776 | 20.776 | 20.788 | 20.8 | 20.772 | 20.751 | 20.736 | 20.723 | 20.744 | 20.732 | 20.744 | 20.744 | 0.9974 | -0.1019 |  | 20.6759 | 20.6231 | 20.6719 | 20.6231 | 20.6111 | 20.636 | 20.648 | 20.5951 | 20.5951 | 20.6201 | 20.6201 | 20.6321 | 20.644 | 20.6161 | 20.5951 | 20.5802 | 20.5672 | 20.5882 | 20.5762 | 20.5882 | 20.5882
12 | Vertical 12 | 20.6221 | 0.030906 | 20.5673 | 20.6884 | -1.08 | 2.4 | 0.6 |  |  | 20.869 | 20.816 | 20.853 | 20.804 | 20.816 | 20.816 | 20.828 | 20.8 | 20.8 | 20.788 | 20.813 | 20.825 | 20.837 | 20.809 | 20.776 | 20.772 | 20.748 | 20.769 | 20.756 | 20.781 | 20.781 | 1.0013 | -0.2077 |  | 20.6884 | 20.6354 | 20.6724 | 20.6233 | 20.6354 | 20.6354 | 20.6474 | 20.6193 | 20.6193 | 20.6073 | 20.6324 | 20.6444 | 20.6564 | 20.6284 | 20.5953 | 20.5913 | 20.5673 | 20.5883 | 20.5753 | 20.6003 | 20.6003
13 | Vertical 13 | 19.2061 | 0.088811 | 19.0293 | 19.3253 | 2.19 | 0.2 | 0.25 |  |  | 19.287 | 19.415 | 19.403 | 19.341 | 19.329 | 19.161 | 19.234 | 19.338 | 19.387 | 19.338 | 19.35 | 19.304 | 19.387 | 19.252 | 19.157 | 19.141 | 19.117 | 19.26 | 19.285 | 19.367 | 19.343 | 0.9932 | 0.0423 |  | 19.1981 | 19.3253 | 19.3134 | 19.2518 | 19.2399 | 19.073 | 19.1455 | 19.2488 | 19.2975 | 19.2488 | 19.2607 | 19.215 | 19.2975 | 19.1634 | 19.069 | 19.0531 | 19.0293 | 19.1713 | 19.1962 | 19.2776 | 19.2538
14 | Vertical 14 | 20.0168 | 0.07051 | 19.8968 | 20.1709 | 2.19 | 0.4 | 0.25 |  |  | 20.137 | 20.183 | 20.268 | 20.122 | 20.134 | 20.06 | 20.085 | 20.13 | 20.179 | 20.155 | 20.167 | 20.118 | 20.167 | 20.029 | 20.02 | 20.053 | 19.992 | 20.001 | 20.16 | 20.16 | 20.05 | 0.9934 | 0.0367 |  | 20.0408 | 20.0865 | 20.1709 | 20.0259 | 20.0378 | 19.9643 | 19.9891 | 20.0338 | 20.0825 | 20.0587 | 20.0706 | 20.0219 | 20.0706 | 19.9335 | 19.9246 | 19.9574 | 19.8968 | 19.9057 | 20.0636 | 20.0636 | 19.9544
15 | Vertical 15 | 20.4632 | 0.035205 | 20.407 | 20.516 | 2.19 | 0.6 | 0.25 |  |  | 20.636 | 20.645 | 20.633 | 20.608 | 20.608 | 20.608 | 20.596 | 20.604 | 20.617 | 20.604 | 20.617 | 20.604 | 20.641 | 20.564 | 20.543 | 20.552 | 20.552 | 20.548 | 20.56 | 20.56 | 20.536 | 0.9998 | -0.1249 |  | 20.507 | 20.516 | 20.504 | 20.479 | 20.479 | 20.479 | 20.467 | 20.475 | 20.488 | 20.475 | 20.488 | 20.475 | 20.512 | 20.435 | 20.414 | 20.423 | 20.423 | 20.419 | 20.431 | 20.431 | 20.407
16 | Vertical 16 | 20.5592 | 0.030692 | 20.5135 | 20.6146 | 2.19 | 0.8 | 0.25 |  |  | 20.612 | 20.608 | 20.682 | 20.657 | 20.657 | 20.645 | 20.62 | 20.604 | 20.629 | 20.641 | 20.653 | 20.653 | 20.678 | 20.589 | 20.58 | 20.589 | 20.589 | 20.634 | 20.634 | 20.609 | 20.585 | 0.9912 | 0.1146 |  | 20.5452 | 20.5412 | 20.6146 | 20.5898 | 20.5898 | 20.5779 | 20.5531 | 20.5373 | 20.5621 | 20.574 | 20.5859 | 20.5859 | 20.6106 | 20.5224 | 20.5135 | 20.5224 | 20.5224 | 20.567 | 20.567 | 20.5422 | 20.5185
17 | Vertical 17 | 20.6453 | 0.01987 | 20.608 | 20.6884 | 2.19 | 1 | 0.25 |  |  | 20.734 | 20.718 | 20.73 | 20.743 | 20.743 | 20.73 | 20.718 | 20.715 | 20.727 | 20.715 | 20.739 | 20.739 | 20.764 | 20.711 | 20.715 | 20.687 | 20.699 | 20.72 | 20.707 | 20.695 | 20.683 | 0.9928 | 0.0739 |  | 20.6586 | 20.6427 | 20.6546 | 20.6676 | 20.6676 | 20.6546 | 20.6427 | 20.6398 | 20.6517 | 20.6398 | 20.6636 | 20.6636 | 20.6884 | 20.6358 | 20.6398 | 20.612 | 20.6239 | 20.6447 | 20.6318 | 20.6199 | 20.608
18 | Vertical 18 | 20.6932 | 0.020941 | 20.6618 | 20.7335 | 2.19 | 1.2 | 0.25 |  |  | 20.807 | 20.804 | 20.792 | 20.828 | 20.816 | 20.804 | 20.779 | 20.788 | 20.788 | 20.776 | 20.788 | 20.8 | 20.825 | 20.784 | 20.776 | 20.76 | 20.76 | 20.769 | 20.769 | 20.769 | 20.756 | 0.996 | -0.0112 |  | 20.7126 | 20.7096 | 20.6976 | 20.7335 | 20.7215 | 20.7096 | 20.6847 | 20.6936 | 20.6936 | 20.6817 | 20.6936 | 20.7056 | 20.7305 | 20.6897 | 20.6817 | 20.6658 | 20.6658 | 20.6747 | 20.6747 | 20.6747 | 20.6618
19 | Vertical 19 | 20.6468 | 0.024438 | 20.6084 | 20.6967 | 2.19 | 1.4 | 0.25 |  |  | 20.746 | 20.706 | 20.73 | 20.767 | 20.767 | 20.743 | 20.718 | 20.715 | 20.715 | 20.702 | 20.739 | 20.751 | 20.776 | 20.723 | 20.715 | 20.687 | 20.699 | 20.72 | 20.707 | 20.707 | 20.707 | 0.9919 | 0.089 |  | 20.667 | 20.6273 | 20.6511 | 20.6878 | 20.6878 | 20.664 | 20.6392 | 20.6362 | 20.6362 | 20.6233 | 20.66 | 20.6719 | 20.6967 | 20.6441 | 20.6362 | 20.6084 | 20.6203 | 20.6412 | 20.6283 | 20.6283 | 20.6283
20 | Vertical 20 | 20.6709 | 0.02814 | 20.6247 | 20.7259 | 2.19 | 1.6 | 0.25 |  |  | 20.82 | 20.779 | 20.792 | 20.804 | 20.792 | 20.767 | 20.767 | 20.776 | 20.776 | 20.739 | 20.764 | 20.788 | 20.825 | 20.772 | 20.764 | 20.736 | 20.723 | 20.769 | 20.744 | 20.732 | 20.732 | 0.9916 | 0.0758 |  | 20.7209 | 20.6803 | 20.6931 | 20.705 | 20.6931 | 20.6684 | 20.6684 | 20.6773 | 20.6773 | 20.6406 | 20.6654 | 20.6892 | 20.7259 | 20.6733 | 20.6654 | 20.6376 | 20.6247 | 20.6703 | 20.6456 | 20.6337 | 20.6337
21 | Vertical 21 | 20.5258 | 0.038867 | 20.4512 | 20.5899 | 2.19 | 1.8 | 0.25 |  |  | 20.467 | 20.479 | 20.455 | 20.467 | 20.439 | 20.402 | 20.439 | 20.448 | 20.402 | 20.395 | 20.407 | 20.419 | 20.444 | 20.428 | 20.391 | 20.367 | 20.339 | 20.4 | 20.388 | 20.376 | 20.348 | 0.9907 | 0.3014 |  | 20.5781 | 20.5899 | 20.5662 | 20.5781 | 20.5503 | 20.5137 | 20.5503 | 20.5592 | 20.5137 | 20.5067 | 20.5186 | 20.5305 | 20.5553 | 20.5394 | 20.5028 | 20.479 | 20.4512 | 20.5117 | 20.4998 | 20.4879 | 20.4602
22 | Vertical 22 | 20.54 | 0.034239 | 20.4718 | 20.5877 | 2.19 | 2 | 0.25 |  |  | 20.553 | 20.54 | 20.54 | 20.553 | 20.537 | 20.5 | 20.549 | 20.521 | 20.488 | 20.493 | 20.493 | 20.517 | 20.53 | 20.514 | 20.502 | 20.465 | 20.437 | 20.473 | 20.486 | 20.461 | 20.458 | 0.9991 | 0.0532 |  | 20.5877 | 20.5747 | 20.5747 | 20.5877 | 20.5717 | 20.5347 | 20.5837 | 20.5557 | 20.5228 | 20.5278 | 20.5278 | 20.5517 | 20.5647 | 20.5487 | 20.5367 | 20.4998 | 20.4718 | 20.5078 | 20.5208 | 20.4958 | 20.4928
23 | Vertical 23 | 20.5418 | 0.034194 | 20.481 | 20.5963 | 2.19 | 2.2 | 0.25 |  |  | 20.528 | 20.54 | 20.528 | 20.528 | 20.512 | 20.488 | 20.537 | 20.497 | 20.463 | 20.481 | 20.468 | 20.493 | 20.493 | 20.489 | 20.477 | 20.44 | 20.424 | 20.449 | 20.449 | 20.461 | 20.445 | 0.994 | 0.1795 |  | 20.5843 | 20.5963 | 20.5843 | 20.5843 | 20.5684 | 20.5446 | 20.5933 | 20.5535 | 20.5197 | 20.5376 | 20.5247 | 20.5495 | 20.5495 | 20.5456 | 20.5336 | 20.4969 | 20.481 | 20.5058 | 20.5058 | 20.5177 | 20.5018
24 | Vertical 24 | 20.538 | 0.030894 | 20.4726 | 20.5885 | 2.19 | 2.4 | 0.25 |  |  | 20.528 | 20.54 | 20.528 | 20.528 | 20.512 | 20.5 | 20.525 | 20.497 | 20.476 | 20.481 | 20.481 | 20.493 | 20.493 | 20.502 | 20.477 | 20.453 | 20.424 | 20.461 | 20.461 | 20.473 | 20.445 | 0.9999 | 0.0506 |  | 20.5765 | 20.5885 | 20.5765 | 20.5765 | 20.5605 | 20.5485 | 20.5735 | 20.5456 | 20.5246 | 20.5296 | 20.5296 | 20.5416 | 20.5416 | 20.5505 | 20.5256 | 20.5016 | 20.4726 | 20.5096 | 20.5096 | 20.5216 | 20.4936
25 | Air 0.1 | 19.1397 | 0.078949 | 18.9274 | 19.2449 | 1.22 | 0.1 | 1.1 |  |  | 18.922 | 19.102 | 19.127 | 19.041 | 19.038 | 18.808 | 19.016 | 19.108 | 19.087 | 19.021 | 19.079 | 19.067 | 19.116 | 18.969 | 18.981 | 18.944 | 18.99 | 19.072 | 19.011 | 19.035 | 18.913 | 0.9952 | 0.2097 |  | 19.0409 | 19.22 | 19.2449 | 19.1593 | 19.1563 | 18.9274 | 19.1344 | 19.226 | 19.2051 | 19.1394 | 19.1971 | 19.1852 | 19.2339 | 19.0876 | 19.0996 | 19.0628 | 19.1085 | 19.1902 | 19.1294 | 19.1533 | 19.0319
26 | Air 0.6 | 20.0381 | 0.048665 | 19.9472 | 20.1082 | 1.22 | 0.6 | 1.1 |  |  | 20.017 | 20.042 | 20.042 | 19.956 | 19.977 | 20.001 | 20.026 | 19.973 | 20.001 | 20.006 | 20.006 | 19.994 | 19.957 | 19.905 | 19.88 | 19.905 | 19.889 | 19.938 | 19.987 | 19.975 | 19.922 | 0.994 | 0.1865 |  | 20.0834 | 20.1082 | 20.1082 | 20.0228 | 20.0436 | 20.0675 | 20.0923 | 20.0397 | 20.0675 | 20.0725 | 20.0725 | 20.0605 | 20.0238 | 19.9721 | 19.9472 | 19.9721 | 19.9562 | 20.0049 | 20.0536 | 20.0417 | 19.989
27 | Air 1.1 | 20.532 | 0.034938 | 20.4784 | 20.6099 | 1.22 | 1.1 | 1.1 |  |  | 20.43 | 20.479 | 20.553 | 20.528 | 20.5 | 20.488 | 20.488 | 20.435 | 20.488 | 20.481 | 20.493 | 20.493 | 20.468 | 20.428 | 20.44 | 20.44 | 20.461 | 20.498 | 20.51 | 20.449 | 20.421 | 0.9962 | 0.135 |  | 20.4874 | 20.5362 | 20.6099 | 20.585 | 20.5571 | 20.5451 | 20.5451 | 20.4923 | 20.5451 | 20.5382 | 20.5501 | 20.5501 | 20.5252 | 20.4854 | 20.4973 | 20.4973 | 20.5182 | 20.5551 | 20.5671 | 20.5063 | 20.4784
28 | Air 1.5 | 20.6389 | 0.026561 | 20.5917 | 20.6861 | 1.22 | 1.5 | 1.1 |  |  | 20.614 | 20.589 | 20.602 | 20.602 | 20.574 | 20.561 | 20.598 | 20.558 | 20.537 | 20.554 | 20.566 | 20.579 | 20.591 | 20.575 | 20.563 | 20.526 | 20.535 | 20.559 | 20.559 | 20.535 | 20.519 | 0.9935 | 0.2061 |  | 20.6861 | 20.6613 | 20.6742 | 20.6742 | 20.6464 | 20.6335 | 20.6702 | 20.6305 | 20.6096 | 20.6265 | 20.6384 | 20.6513 | 20.6633 | 20.6474 | 20.6354 | 20.5987 | 20.6076 | 20.6315 | 20.6315 | 20.6076 | 20.5917
29 | Cieling | 20.6045 | 0.027733 | 20.5561 | 20.6465 | 0 | 2.46 | 0.6 |  |  | 20.602 | 20.602 | 20.602 | 20.602 | 20.574 | 20.586 | 20.61 | 20.558 | 20.549 | 20.566 | 20.566 | 20.591 | 20.579 | 20.575 | 20.551 | 20.538 | 20.522 | 20.547 | 20.535 | 20.547 | 20.519 | 0.9933 | 0.1746 |  | 20.6386 | 20.6386 | 20.6386 | 20.6386 | 20.6108 | 20.6227 | 20.6465 | 20.5949 | 20.5859 | 20.6028 | 20.6028 | 20.6276 | 20.6157 | 20.6117 | 20.5879 | 20.575 | 20.5591 | 20.5839 | 20.572 | 20.5839 | 20.5561
30 | Floor | 20.7399 | 0.016649 | 20.7144 | 20.772 | 1.85 | 0 | 0.6 |  |  | 20.724 | 20.724 | 20.712 | 20.699 | 20.696 | 20.696 | 20.708 | 20.692 | 20.696 | 20.701 | 20.689 | 20.689 | 20.689 | 20.685 | 20.685 | 20.673 | 20.669 | 20.669 | 20.694 | 20.669 | 20.666 | 0.9921 | 0.2117 |  | 20.772 | 20.772 | 20.7601 | 20.7472 | 20.7442 | 20.7442 | 20.7561 | 20.7402 | 20.7442 | 20.7492 | 20.7373 | 20.7373 | 20.7373 | 20.7333 | 20.7333 | 20.7214 | 20.7174 | 20.7174 | 20.7422 | 20.7174 | 20.7144
31 | Floor | 24.1826 | 0.01708 | 24.1565 | 24.2176 | 0.59 | 0 | 0.6 |  |  | 24.146 | 24.149 | 24.158 | 24.122 | 24.107 | 24.13 | 24.139 | 24.127 | 24.139 | 24.115 | 24.115 | 24.111 | 24.111 | 24.123 | 24.096 | 24.108 | 24.096 | 24.113 | 24.104 | 24.137 | 24.125 | 0.9847 | 0.4292 |  | 24.2058 | 24.2087 | 24.2176 | 24.1821 | 24.1674 | 24.19 | 24.1989 | 24.1871 | 24.1989 | 24.1752 | 24.1752 | 24.1713 | 24.1713 | 24.1831 | 24.1565 | 24.1683 | 24.1565 | 24.1733 | 24.1644 | 24.1969 | 24.1851
32 | Floor | 19.7082 | 0.023795 | 19.6787 | 19.7573 | 0 | 0 | 0.6 |  |  | 19.662 | 19.678 | 19.662 | 19.626 | 19.647 | 19.647 | 19.618 | 19.618 | 19.643 | 19.618 | 19.631 | 19.615 | 19.627 | 19.676 | 19.611 | 19.611 | 19.623 | 19.641 | 19.644 | 19.69 | 19.665 | 0.9948 | 0.1697 |  | 19.7295 | 19.7454 | 19.7295 | 19.6936 | 19.7145 | 19.7145 | 19.6857 | 19.6857 | 19.7106 | 19.6857 | 19.6986 | 19.6827 | 19.6946 | 19.7434 | 19.6787 | 19.6787 | 19.6907 | 19.7086 | 19.7116 | 19.7573 | 19.7324
33 | Mid cieling | 20.7443 | 0.023637 | 20.7045 | 20.7783 | 1.22 | 2.46 | 0.6 |  |  | 20.712 | 20.715 | 20.712 | 20.712 | 20.684 | 20.708 | 20.705 | 20.692 | 20.692 | 20.68 | 20.668 | 20.677 | 20.677 | 20.677 | 20.673 | 20.661 | 20.661 | 20.653 | 20.657 | 20.641 | 20.641 | 0.9972 | 0.1213 |  | 20.7753 | 20.7783 | 20.7753 | 20.7753 | 20.7474 | 20.7713 | 20.7683 | 20.7554 | 20.7554 | 20.7434 | 20.7314 | 20.7404 | 20.7404 | 20.7404 | 20.7364 | 20.7244 | 20.7244 | 20.7165 | 20.7205 | 20.7045 | 20.7045
34 | Window wall | 20.9403 | 0.022743 | 20.8987 | 20.9814 | 0.59 | 1.23 | 1.2 |  |  | 20.892 | 20.896 | 20.905 | 20.892 | 20.877 | 20.889 | 20.885 | 20.861 | 20.861 | 20.861 | 20.861 | 20.857 | 20.857 | 20.857 | 20.841 | 20.866 | 20.841 | 20.846 | 20.838 | 20.834 | 20.822 | 0.9966 | 0.1475 |  | 20.9685 | 20.9725 | 20.9814 | 20.9685 | 20.9535 | 20.9655 | 20.9615 | 20.9376 | 20.9376 | 20.9376 | 20.9376 | 20.9336 | 20.9336 | 20.9336 | 20.9176 | 20.9426 | 20.9176 | 20.9226 | 20.9147 | 20.9107 | 20.8987
35 | Window wall | 20.8929 | 0.019687 | 20.8532 | 20.9269 | 1.85 | 1.23 | 1.2 |  |  | 20.843 | 20.847 | 20.831 | 20.831 | 20.815 | 20.828 | 20.836 | 20.824 | 20.824 | 20.812 | 20.799 | 20.808 | 20.808 | 20.82 | 20.804 | 20.804 | 20.792 | 20.797 | 20.789 | 20.785 | 20.773 | 0.9957 | 0.1695 |  | 20.9229 | 20.9269 | 20.9109 | 20.9109 | 20.895 | 20.9079 | 20.9159 | 20.904 | 20.904 | 20.892 | 20.8791 | 20.888 | 20.888 | 20.9 | 20.884 | 20.884 | 20.8721 | 20.8771 | 20.8691 | 20.8651 | 20.8532
36 | Door wall | 20.3123 | 0.026435 | 20.2626 | 20.3577 | 1.85 | 1.23 | 0 |  |  | 20.222 | 20.226 | 20.21 | 20.21 | 20.194 | 20.206 | 20.203 | 20.191 | 20.191 | 20.178 | 20.169 | 20.175 | 20.175 | 20.163 | 20.159 | 20.159 | 20.159 | 20.176 | 20.146 | 20.142 | 20.13 | 0.9912 | 0.3097 |  | 20.3537 | 20.3577 | 20.3419 | 20.3419 | 20.326 | 20.3379 | 20.3349 | 20.323 | 20.323 | 20.3101 | 20.3012 | 20.3072 | 20.3072 | 20.2953 | 20.2913 | 20.2913 | 20.2913 | 20.3082 | 20.2784 | 20.2745 | 20.2626
37 | Door wall | 20.4045 | 0.031214 | 20.3484 | 20.4575 | 0.59 | 1.23 | 0 |  |  | 20.283 | 20.287 | 20.283 | 20.271 | 20.255 | 20.243 | 20.252 | 20.239 | 20.252 | 20.227 | 20.227 | 20.224 | 20.236 | 20.224 | 20.208 | 20.208 | 20.208 | 20.213 | 20.192 | 20.188 | 20.176 | 0.9828 | 0.5194 |  | 20.4535 | 20.4575 | 20.4535 | 20.4417 | 20.426 | 20.4142 | 20.4231 | 20.4103 | 20.4231 | 20.3985 | 20.3985 | 20.3955 | 20.4073 | 20.3955 | 20.3798 | 20.3798 | 20.3798 | 20.3847 | 20.3641 | 20.3602 | 20.3484
38 | Upper outlet | 20.6836 | 0.043974 | 20.6211 | 20.7932 | 2.44 | 1.84 | 0.6 |  |  | 20.675 | 20.568 | 20.626 | 20.553 | 20.561 | 20.574 | 20.643 | 20.521 | 20.533 | 20.546 | 20.582 | 20.591 | 20.591 | 20.542 | 20.502 | 20.514 | 20.526 | 20.555 | 20.51 | 20.58 | 20.568 | 0.9946 | 0.2298 |  | 20.7932 | 20.6867 | 20.7444 | 20.6718 | 20.6798 | 20.6927 | 20.7613 | 20.64 | 20.6519 | 20.6649 | 20.7007 | 20.7096 | 20.7096 | 20.6609 | 20.6211 | 20.633 | 20.645 | 20.6738 | 20.629 | 20.6987 | 20.6867
39 | Lower outlet | 20.234 | 0.086104 | 20.0809 | 20.3493 | 2.44 | 0.63 | 0.6 |  |  | 20.198 | 20.168 | 20.185 | 20.017 | 20.173 | 20.112 | 20.191 | 20.108 | 20.084 | 20.035 | 20.203 | 19.982 | 20.068 | 20.019 | 19.954 | 20.089 | 20.052 | 19.947 | 20.217 | 20.118 | 20.201 | 0.9939 | 0.2556 |  | 20.3304 | 20.3006 | 20.3175 | 20.1505 | 20.3055 | 20.2449 | 20.3234 | 20.2409 | 20.2171 | 20.1684 | 20.3354 | 20.1157 | 20.2012 | 20.1525 | 20.0879 | 20.2221 | 20.1853 | 20.0809 | 20.3493 | 20.2509 | 20.3334
40 | Back wall | 20.8452 | 0.023541 | 20.7952 | 20.891 | 2.44 | 1.23 | 0.6 |  |  | 20.77 | 20.786 | 20.77 | 20.77 | 20.754 | 20.754 | 20.75 | 20.75 | 20.75 | 20.729 | 20.741 | 20.735 | 20.747 | 20.735 | 20.722 | 20.71 | 20.722 | 20.724 | 20.718 | 20.715 | 20.69 | 0.9974 | 0.159 |  | 20.875 | 20.891 | 20.875 | 20.875 | 20.859 | 20.859 | 20.855 | 20.855 | 20.855 | 20.8341 | 20.8461 | 20.8401 | 20.8521 | 20.8401 | 20.8271 | 20.8152 | 20.8271 | 20.8291 | 20.8231 | 20.8201 | 20.7952
| Air velocities: |  | Dantec Dynamics Indoor Flow System with 5 54T21 Omnidirectional Transducers.
| Position |  | Air velocities (m/s) |  |  |  | Coordinates |  |  |  | 157.5 | 156.8 | 155.5 | 152.9 | 154.8 | 156.4 | 154 | 155.1 | 152.9 | 154.2 | 154.6 | 152.6 | 154.2 | 156.7 | 152.3 | 154.6 | 154.4 | 151 | 151.1 | 151.1 | 153.9 |  | L. Foot |  | 154.1238 | 1.8839 | 151 | 157.5
|  | va [m/s] | STD [m/s] | Tu % |  | x | y | z |  |  | 160.3 | 161.2 | 162.9 | 159.4 | 159.9 | 161.9 | 161.2 | 162 | 161.7 | 161.9 | 162.2 | 158.6 | 162.4 | 164.2 | 160.2 | 161.7 | 161.9 | 157.7 | 157.3 | 158.9 | 159.2 |  | R. Foot |  | 160.7952 | 1.7854 | 157.3 | 164.2
1 | Air vel. 1 | 0.292 | 0.017 | 5.93 |  | 0.19 | 1.3 | 0 |  |  | 144.7 | 145.2 | 144.6 | 144.1 | 144.4 | 145 | 145.2 | 144.4 | 145 | 144.8 | 144.7 | 144.9 | 145 | 144.8 | 145.1 | 145.2 | 145.3 | 145.3 | 144.9 | 144.4 | 144.6 |  | L. Low leg |  | 144.8381 | 0.33537 | 144.1 | 145.3
2 | Air vel. 2 | 0.269 | 0.014 | 5.195 |  | 0.19 | 1.1 | 0 |  |  | 147 | 146.6 | 146 | 144.6 | 144.9 | 146.7 | 146.4 | 145.9 | 145.4 | 146.7 | 146 | 145.6 | 146.2 | 146.7 | 145.4 | 146.3 | 145.9 | 144.7 | 145.1 | 145.6 | 145.9 |  | R. Low leg |  | 145.8857 | 0.6923 | 144.6 | 147
3 | Air vel. 3 | 0.254 | 0.01 | 3.815 |  | 0.19 | 0.875 | 0 |  |  | 101 | 101.5 | 101 | 100.8 | 101.6 | 101 | 100.4 | 101.1 | 101 | 100.8 | 101 | 101.5 | 101.4 | 101.5 | 101 | 101.6 | 102.4 | 101.3 | 101.9 | 100.6 | 101.8 |  | L. Thigh |  | 101.2476 | 0.47183 | 100.4 | 102.4
4 | Air vel. 4 | 0.243 | 0.009 | 3.551 |  | 0.19 | 0.55 | 0 |  |  | 106.1 | 105.3 | 105.4 | 106.1 | 105.6 | 104.9 | 105.7 | 105.1 | 105.8 | 104.5 | 105.4 | 105.1 | 105.7 | 105.7 | 105.7 | 106.1 | 106.5 | 104.6 | 105.6 | 105 | 105.5 |  | R. Thigh |  | 105.4952 | 0.50742 | 104.5 | 106.5
5 | Air vel. 5 | 0.278 | 0.036 | 12.962 |  | 0.19 | 0.275 | 0 |  |  | 114.6 | 114.8 | 114.1 | 114.9 | 114.3 | 115 | 114.6 | 114.4 | 114.6 | 114 | 114.6 | 114.9 | 115.2 | 114.2 | 115.1 | 114.5 | 114.4 | 114.8 | 115.6 | 115.1 | 115 |  | Pelvis |  | 114.7 | 0.39875 | 114 | 115.6
6 | Air vel. 6 | 0.186 | 0.077 | 41.344 |  | 2.19 | 1.3 | 0 |  |  | 120.1 | 120.3 | 120.5 | 120.2 | 120.5 | 120.3 | 120.5 | 120.2 | 120 | 119.7 | 120.2 | 120.6 | 121.1 | 120.5 | 120.4 | 120.6 | 121.1 | 121 | 121.1 | 121.1 | 121 |  | Head |  | 120.5238 | 0.40976 | 119.7 | 121.1
7 | Air vel. 7 | 0.228 | 0.057 | 24.867 |  | 2.19 | 1.1 | 0 |  |  | 71.8 | 71.9 | 72.2 | 71.9 | 72.3 | 72.4 | 72.2 | 72 | 72.1 | 71.9 | 72.2 | 71.8 | 72.6 | 72.4 | 72.4 | 72.5 | 72.7 | 72.5 | 72.5 | 73 | 72.8 |  | Top of head |  | 72.2905 | 0.3375 | 71.8 | 73
8 | Air vel. 8 | 0.72 | 0.053 | 7.357 |  | 2.19 | 0.875 | 0 |  |  | 164.1 | 163.5 | 164.8 | 164.3 | 164.3 | 163.6 | 163.3 | 163.2 | 163.4 | 163.5 | 164.3 | 164.6 | 165.1 | 166.1 | 165.7 | 165 | 165.1 | 163.6 | 164.4 | 165 | 165.9 |  | L. Hand |  | 164.419 | 0.87728 | 163.2 | 166.1
9 | Air vel. 9 | 0.982 | 0.043 | 4.383 |  | 2.19 | 0.55 | 0 |  |  | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.5 | 187.6 | 187.6 | 187.6 | 186.4 | 187.4 | 187.3 | 187.5 | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 |  | R. Hand |  | 187.5095 | 0.26628 | 186.4 | 187.6
10 | Air vel. 10 | 0.469 | 0.032 | 6.849 |  | 2.19 | 0.275 | 0 |  |  | 152.3 | 151.9 | 154.1 | 152.8 | 152.9 | 153.3 | 151.2 | 152.1 | 152.4 | 152.8 | 153.6 | 151.7 | 153.7 | 156 | 153.9 | 153 | 153.7 | 149.9 | 151.3 | 154.2 | 155 |  | L. Forearm |  | 152.9429 | 1.3822 | 149.9 | 156
[11 empty] | 135.1 | 134.5 | 135 | 135.5 | 135.2 | 133.8 | 135.1 | 134.7 | 135.8 | 131.2 | 134.1 | 134.6 | 135.5 | 134.8 | 135.6 | 136.4 | 137.6 | 137.4 | 137.2 | 134.2 | 133.6 |  | R. Forearm |  | 135.0905 | 1.4237 | 131.2 | 137.6
[11 empty] | 122 | 122.4 | 123.7 | 123.8 | 124.3 | 123.3 | 123.6 | 122.9 | 123.7 | 122.8 | 122.5 | 124.1 | 123.9 | 123.7 | 123.7 | 124.7 | 125.1 | 123.5 | 124.3 | 124.7 | 123.8 |  | L. Upper arm |  | 123.6429 | 0.79093 | 122 | 125.1
[11 empty] | 130.4 | 130.1 | 131.9 | 131.5 | 131.4 | 131 | 131.2 | 130.8 | 131.2 | 130.3 | 130.9 | 132.8 | 132 | 131.6 | 131.6 | 131.9 | 132.6 | 130.8 | 131.8 | 132.5 | 131.4 |  | R. Upper arm |  | 131.4143 | 0.73572 | 130.1 | 132.8
[11 empty] | 118 | 117.9 | 118.7 | 117.9 | 118.2 | 118.1 | 118.2 | 118 | 118 | 118.5 | 118.3 | 119 | 118.6 | 118.6 | 118.4 | 118.5 | 118.5 | 118.5 | 119 | 118.7 | 118.7 |  | Chest |  | 118.3952 | 0.33686 | 117.9 | 119
[11 empty] | 110.6 | 110.1 | 111.8 | 112.6 | 112.9 | 113 | 112.3 | 112.2 | 112.9 | 112.5 | 111.8 | 112.9 | 113.8 | 112.3 | 113.1 | 113.4 | 113.1 | 112.5 | 112.8 | 114.2 | 113.5 |  | Back |  | 112.5857 | 0.95671 | 110.1 | 114.2
[11 empty] | 123.6 | 123.5 | 123.9 | 123.6 | 123.8 | 123.8 | 123.7 | 123.5 | 123.7 | 123.3 | 123.6 | 123.8 | 124.3 | 124.2 | 123.9 | 124.2 | 124.5 | 123.5 | 124 | 123.9 | 124.1 |  | All |  | 123.8286 | 0.30519 | 123.3 | 124.5

## HL5@va0.27ta20
Manikin heat loss in windtunnel
| Nom. Inlet velocity |  | 0.2 | m/s | Nom. Air temperature |  | 20 | ºC
| Mean Inlet velocity |  | 0.2672 | m/s | Mean Air temp. |  | 20.341 | ºC
[10 empty] | 1 |  | 2 | [15 empty] | 2
| Std. dev. Inlet vel. |  | 0.0172 | m/s | Std. dev. Air temp. |  | 0.046184 | ºC
1
| Mean Inlet Turb. intens. |  | 6.2906 | % | Mean Wall temp. |  | 20.9256 | ºC
| Relative Humidity |  | 35 | % | Air Pressure |  | 1027.15 | mbar | 4 |  |  | 3 | [12 empty] | 6 | [6 empty] | 5
| Thermal manikin: |  | Comfortina, No clothing, Software version 3.0.30. | [6 empty] | 6 | [17 empty] | 3
| Body Segments |  | Heat loss (W/m2) | [30 empty] | H L (W/m2) | Zones | No
|  | Q [W/m2] | STD [W/m2] | Min | Max | [7 empty] | 8 |  |  |  | 10 | [7 empty] | 10 | [6 empty] | 11 |  | 124.0048 | Total | 18
1 | L. Foot | 153.9857 | 2.2064 | 150.1 | 158.7 | [28 empty] | 72.419 | Scalp | 9 | 1
2 | R. Foot | 160.0952 | 1.7597 | 156.7 | 163 |  |  |  |  | 17 | [23 empty] | 120.9714 | Face | 8 | 2
3 | L. Low leg | 145.2095 | 0.55579 | 144.2 | 146.3 | [28 empty] | 118.6286 | Chest | 16 | 3
4 | R. Low leg | 146.0333 | 0.89238 | 144.4 | 147.3 | [5 empty] | 18 |  |  |  |  | 12 | [9 empty] | 12 |  | 18 |  | 11 |  |  |  | 111.9429 | Up. back | 17 | 4
5 | L. Thigh | 101.9762 | 0.50981 | 100.9 | 103.4 | [28 empty] | 123.5143 | L U arm | 14 | 5
6 | R. Thigh | 106.1905 | 0.79114 | 105 | 107.8 | [28 empty] | 131.4571 | R U arm | 15 | 6
7 | Pelvis | 114.8381 | 0.52866 | 113.5 | 115.5 | [28 empty] | 151.8667 | L L arm | 12 | 7
8 | Head | 120.9714 | 0.52644 | 119.9 | 122 | [28 empty] | 136.5667 | R L arm | 13 | 8
9 | Top of head | 72.419 | 0.20401 | 72 | 72.9 | [14 empty] | 14 | [5 empty] | 14 |  |  |  | 13 |  |  |  | 164.0667 | L hand | 10 | 9
10 | L. Hand | 164.0667 | 0.92592 | 162.2 | 165.9 | [28 empty] | 187.6429 | R hand | 11 | 10
11 | R. Hand | 187.6429 | 0.050709 | 187.6 | 187.7 | [28 empty] | 101.9762 | L thigh | 5 | 11
12 | L. Forearm | 151.8667 | 1.4735 | 149.7 | 154.8 |  |  |  | y | [19 empty] | y |  |  |  |  | 106.1905 | R thigh | 6 | 12
13 | R. Forearm | 136.5667 | 1.0561 | 133.6 | 138.4 | [14 empty] | 16 | [5 empty] | 16 |  |  |  | 15 |  |  |  | 145.2095 | L calf | 3 | 13
14 | L. Upper arm | 123.5143 | 0.52942 | 122.6 | 124.4 | [28 empty] | 146.0333 | R calf | 4 | 14
15 | R. Upper arm | 131.4571 | 0.49857 | 130.5 | 132.5 |  |  |  | z |  |  | x | [13 empty] | z |  |  | x |  |  |  |  | 153.9857 | L foot | 1 | 15
16 | Chest | 118.6286 | 0.34662 | 118 | 119.3 | [28 empty] | 160.0952 | R foot | 2 | 16
17 | Back | 111.9429 | 0.79093 | 110.4 | 113.1 | [6 empty] | Corresponding zones on MANIKIN2 and 3 | [21 empty] | 111.9429 | Lo. back | 17 | 17
18 | All | 124.0048 | 0.36121 | 123.3 | 124.6 | [28 empty] | 114.8381 | Seat | 7 | 18
| Temperatures: |  | Fluke Helios Plus 2287A with 40 Thermocouple Channels.
| Position |  | Temperatures (ºC) |  |  |  | Coordinates |  |  |  | 1555-1575
|  | ta [ºC] | STD [ºC] | Min | Max | x | y | z | [23 empty] | a | b | T=ax+b
1 | Vertical 1 | 19.5536 | 0.060689 | 19.458 | 19.6666 | -1.08 | 0.2 | 0.6 |  |  | 19.558 | 19.533 | 19.546 | 19.497 | 19.595 | 19.423 | 19.558 | 19.546 | 19.53 | 19.542 | 19.432 | 19.477 | 19.432 | 19.432 | 19.44 | 19.502 | 19.551 | 19.572 | 19.633 | 19.51 | 19.596 | 0.9933 | 0.1651 |  | 19.5921 | 19.5672 | 19.5801 | 19.5315 | 19.6288 | 19.458 | 19.5921 | 19.5801 | 19.5642 | 19.5762 | 19.4669 | 19.5116 | 19.4669 | 19.4669 | 19.4749 | 19.5364 | 19.5851 | 19.606 | 19.6666 | 19.5444 | 19.6298
2 | Vertical 2 | 19.839 | 0.04485 | 19.7771 | 19.9142 | -1.08 | 0.4 | 0.6 |  |  | 19.897 | 19.861 | 19.885 | 19.815 | 19.897 | 19.803 | 19.824 | 19.803 | 19.811 | 19.833 | 19.799 | 19.817 | 19.762 | 19.762 | 19.759 | 19.759 | 19.771 | 19.813 | 19.875 | 19.838 | 19.862 | 0.9932 | 0.1525 |  | 19.9142 | 19.8784 | 19.9023 | 19.8328 | 19.9142 | 19.8208 | 19.8417 | 19.8208 | 19.8288 | 19.8506 | 19.8169 | 19.8347 | 19.7801 | 19.7801 | 19.7771 | 19.7771 | 19.7891 | 19.8308 | 19.8924 | 19.8556 | 19.8794
3 | Vertical 3 | 20.1212 | 0.080942 | 20.005 | 20.2767 | -1.08 | 0.6 | 0.6 |  |  | 20.289 | 20.155 | 20.289 | 20.24 | 20.24 | 20.069 | 20.13 | 20.106 | 20.065 | 20.102 | 20.041 | 20.16 | 20.139 | 20.016 | 20.025 | 20.037 | 20.074 | 20.144 | 20.168 | 20.168 | 20.131 | 0.9951 | 0.0871 |  | 20.2767 | 20.1433 | 20.2767 | 20.2279 | 20.2279 | 20.0578 | 20.1185 | 20.0946 | 20.0538 | 20.0906 | 20.0299 | 20.1483 | 20.1274 | 20.005 | 20.014 | 20.0259 | 20.0627 | 20.1324 | 20.1563 | 20.1563 | 20.1195
4 | Vertical 4 | 20.314 | 0.08629 | 20.1703 | 20.4709 | -1.08 | 0.8 | 0.6 |  |  | 20.408 | 20.252 | 20.408 | 20.384 | 20.47 | 20.167 | 20.277 | 20.289 | 20.224 | 20.31 | 20.322 | 20.426 | 20.298 | 20.2 | 20.258 | 20.184 | 20.245 | 20.34 | 20.398 | 20.41 | 20.278 | 0.9922 | 0.1606 |  | 20.4094 | 20.2546 | 20.4094 | 20.3856 | 20.4709 | 20.1703 | 20.2794 | 20.2913 | 20.2269 | 20.3122 | 20.3241 | 20.4273 | 20.3003 | 20.203 | 20.2606 | 20.1872 | 20.2477 | 20.3419 | 20.3995 | 20.4114 | 20.2804
5 | Vertical 5 | 20.4289 | 0.042798 | 20.3538 | 20.521 | -1.08 | 1 | 0.6 |  |  | 20.604 | 20.519 | 20.604 | 20.568 | 20.629 | 20.531 | 20.555 | 20.543 | 20.515 | 20.552 | 20.54 | 20.56 | 20.478 | 20.491 | 20.511 | 20.462 | 20.475 | 20.532 | 20.544 | 20.544 | 20.52 | 1.0015 | -0.1389 |  | 20.496 | 20.4109 | 20.496 | 20.46 | 20.521 | 20.4229 | 20.4469 | 20.4349 | 20.4069 | 20.4439 | 20.4319 | 20.4519 | 20.3698 | 20.3828 | 20.4029 | 20.3538 | 20.3668 | 20.4239 | 20.4359 | 20.4359 | 20.4119
6 | Vertical 6 | 20.4847 | 0.043047 | 20.4097 | 20.5598 | -1.08 | 1.2 | 0.6 |  |  | 20.604 | 20.555 | 20.617 | 20.58 | 20.617 | 20.629 | 20.58 | 20.555 | 20.576 | 20.576 | 20.552 | 20.56 | 20.478 | 20.503 | 20.524 | 20.499 | 20.499 | 20.532 | 20.508 | 20.52 | 20.557 | 0.994 | 0.0546 |  | 20.535 | 20.4863 | 20.5479 | 20.5111 | 20.5479 | 20.5598 | 20.5111 | 20.4863 | 20.5071 | 20.5071 | 20.4833 | 20.4912 | 20.4097 | 20.4346 | 20.4555 | 20.4306 | 20.4306 | 20.4634 | 20.4396 | 20.4515 | 20.4883
7 | Vertical 7 | 20.5361 | 0.034115 | 20.4787 | 20.6037 | -1.08 | 1.4 | 0.6 |  |  | 20.653 | 20.617 | 20.629 | 20.604 | 20.617 | 20.629 | 20.592 | 20.58 | 20.613 | 20.601 | 20.576 | 20.56 | 20.527 | 20.552 | 20.548 | 20.573 | 20.573 | 20.569 | 20.532 | 20.544 | 20.593 | 0.9922 | 0.1118 |  | 20.6037 | 20.568 | 20.5799 | 20.5551 | 20.568 | 20.5799 | 20.5432 | 20.5313 | 20.564 | 20.5521 | 20.5273 | 20.5114 | 20.4787 | 20.5035 | 20.4995 | 20.5243 | 20.5243 | 20.5204 | 20.4837 | 20.4956 | 20.5442
8 | Vertical 8 | 20.5553 | 0.03404 | 20.495 | 20.6041 | -1.08 | 1.6 | 0.6 |  |  | 20.727 | 20.715 | 20.715 | 20.702 | 20.715 | 20.727 | 20.69 | 20.69 | 20.711 | 20.662 | 20.662 | 20.658 | 20.625 | 20.662 | 20.658 | 20.683 | 20.683 | 20.655 | 20.618 | 20.618 | 20.667 | 1.0008 | -0.1395 |  | 20.6041 | 20.5921 | 20.5921 | 20.5791 | 20.5921 | 20.6041 | 20.5671 | 20.5671 | 20.5881 | 20.539 | 20.539 | 20.535 | 20.502 | 20.539 | 20.535 | 20.56 | 20.56 | 20.532 | 20.495 | 20.495 | 20.544
9 | Vertical 9 | 20.5547 | 0.032009 | 20.4991 | 20.6084 | -1.08 | 1.8 | 0.6 |  |  | 20.751 | 20.739 | 20.739 | 20.715 | 20.715 | 20.739 | 20.715 | 20.715 | 20.711 | 20.686 | 20.674 | 20.671 | 20.662 | 20.699 | 20.683 | 20.707 | 20.695 | 20.691 | 20.642 | 20.642 | 20.655 | 1.0022 | -0.1883 |  | 20.6084 | 20.5963 | 20.5963 | 20.5723 | 20.5723 | 20.5963 | 20.5723 | 20.5723 | 20.5683 | 20.5432 | 20.5312 | 20.5282 | 20.5192 | 20.5562 | 20.5402 | 20.5643 | 20.5522 | 20.5482 | 20.4991 | 20.4991 | 20.5121
10 | Vertical 10 | 20.5557 | 0.034249 | 20.494 | 20.6148 | -1.08 | 2 | 0.6 |  |  | 20.776 | 20.751 | 20.776 | 20.727 | 20.727 | 20.751 | 20.727 | 20.727 | 20.748 | 20.699 | 20.699 | 20.695 | 20.686 | 20.735 | 20.72 | 20.707 | 20.72 | 20.704 | 20.667 | 20.655 | 20.655 | 0.9986 | -0.1321 |  | 20.6148 | 20.5898 | 20.6148 | 20.5659 | 20.5659 | 20.5898 | 20.5659 | 20.5659 | 20.5869 | 20.5379 | 20.5379 | 20.5339 | 20.5249 | 20.5739 | 20.5589 | 20.5459 | 20.5589 | 20.5429 | 20.506 | 20.494 | 20.494
11 | Vertical 11 | 20.5651 | 0.031372 | 20.4994 | 20.6201 | -1.08 | 2.2 | 0.6 |  |  | 20.776 | 20.763 | 20.751 | 20.751 | 20.739 | 20.763 | 20.727 | 20.727 | 20.735 | 20.723 | 20.699 | 20.699 | 20.711 | 20.732 | 20.732 | 20.695 | 20.707 | 20.691 | 20.691 | 20.671 | 20.655 | 0.9974 | -0.1019 |  | 20.6201 | 20.6071 | 20.5951 | 20.5951 | 20.5832 | 20.6071 | 20.5712 | 20.5712 | 20.5792 | 20.5672 | 20.5433 | 20.5433 | 20.5553 | 20.5762 | 20.5762 | 20.5393 | 20.5513 | 20.5353 | 20.5353 | 20.5154 | 20.4994
12 | Vertical 12 | 20.5839 | 0.029802 | 20.5392 | 20.6444 | -1.08 | 2.4 | 0.6 |  |  | 20.825 | 20.788 | 20.8 | 20.8 | 20.788 | 20.8 | 20.776 | 20.763 | 20.772 | 20.748 | 20.76 | 20.748 | 20.735 | 20.793 | 20.768 | 20.732 | 20.744 | 20.728 | 20.74 | 20.72 | 20.728 | 1.0013 | -0.2077 |  | 20.6444 | 20.6073 | 20.6193 | 20.6193 | 20.6073 | 20.6193 | 20.5953 | 20.5823 | 20.5913 | 20.5673 | 20.5793 | 20.5673 | 20.5543 | 20.6123 | 20.5873 | 20.5513 | 20.5633 | 20.5472 | 20.5593 | 20.5392 | 20.5472
13 | Vertical 13 | 19.2523 | 0.073997 | 19.1107 | 19.37 | 2.19 | 0.2 | 0.25 |  |  | 19.46 | 19.313 | 19.338 | 19.399 | 19.435 | 19.387 | 19.289 | 19.374 | 19.334 | 19.346 | 19.239 | 19.322 | 19.395 | 19.199 | 19.223 | 19.281 | 19.269 | 19.302 | 19.425 | 19.428 | 19.413 | 0.9932 | 0.0423 |  | 19.37 | 19.224 | 19.2488 | 19.3094 | 19.3451 | 19.2975 | 19.2001 | 19.2846 | 19.2448 | 19.2567 | 19.1505 | 19.2329 | 19.3054 | 19.1107 | 19.1346 | 19.1922 | 19.1803 | 19.213 | 19.3352 | 19.3382 | 19.3233
14 | Vertical 14 | 20.0965 | 0.072884 | 19.9941 | 20.2405 | 2.19 | 0.4 | 0.25 |  |  | 20.338 | 20.265 | 20.265 | 20.228 | 20.228 | 20.228 | 20.118 | 20.204 | 20.127 | 20.151 | 20.09 | 20.151 | 20.261 | 20.098 | 20.123 | 20.233 | 20.098 | 20.107 | 20.217 | 20.233 | 20.291 | 0.9934 | 0.0367 |  | 20.2405 | 20.168 | 20.168 | 20.1312 | 20.1312 | 20.1312 | 20.0219 | 20.1074 | 20.0309 | 20.0547 | 19.9941 | 20.0547 | 20.164 | 20.0021 | 20.0269 | 20.1362 | 20.0021 | 20.011 | 20.1203 | 20.1362 | 20.1938
15 | Vertical 15 | 20.4577 | 0.021566 | 20.415 | 20.512 | 2.19 | 0.6 | 0.25 |  |  | 20.641 | 20.617 | 20.604 | 20.604 | 20.604 | 20.604 | 20.592 | 20.592 | 20.589 | 20.576 | 20.576 | 20.601 | 20.576 | 20.573 | 20.573 | 20.573 | 20.573 | 20.544 | 20.569 | 20.56 | 20.581 | 0.9998 | -0.1249 |  | 20.512 | 20.488 | 20.475 | 20.475 | 20.475 | 20.475 | 20.463 | 20.463 | 20.46 | 20.447 | 20.447 | 20.472 | 20.447 | 20.444 | 20.444 | 20.444 | 20.444 | 20.415 | 20.44 | 20.431 | 20.452
16 | Vertical 16 | 20.5676 | 0.028833 | 20.5145 | 20.6186 | 2.19 | 0.8 | 0.25 |  |  | 20.678 | 20.617 | 20.629 | 20.653 | 20.666 | 20.666 | 20.629 | 20.641 | 20.662 | 20.625 | 20.625 | 20.686 | 20.662 | 20.585 | 20.597 | 20.646 | 20.609 | 20.581 | 20.63 | 20.622 | 20.618 | 0.9912 | 0.1146 |  | 20.6106 | 20.5502 | 20.5621 | 20.5859 | 20.5987 | 20.5987 | 20.5621 | 20.574 | 20.5948 | 20.5581 | 20.5581 | 20.6186 | 20.5948 | 20.5185 | 20.5303 | 20.5789 | 20.5422 | 20.5145 | 20.5631 | 20.5551 | 20.5512
17 | Vertical 17 | 20.6197 | 0.023897 | 20.5802 | 20.6636 | 2.19 | 1 | 0.25 |  |  | 20.739 | 20.715 | 20.702 | 20.739 | 20.715 | 20.715 | 20.715 | 20.69 | 20.711 | 20.686 | 20.699 | 20.711 | 20.686 | 20.671 | 20.683 | 20.671 | 20.671 | 20.655 | 20.679 | 20.658 | 20.679 | 0.9928 | 0.0739 |  | 20.6636 | 20.6398 | 20.6268 | 20.6636 | 20.6398 | 20.6398 | 20.6398 | 20.6149 | 20.6358 | 20.611 | 20.6239 | 20.6358 | 20.611 | 20.5961 | 20.608 | 20.5961 | 20.5961 | 20.5802 | 20.604 | 20.5832 | 20.604
18 | Vertical 18 | 20.6588 | 0.024662 | 20.613 | 20.7056 | 2.19 | 1.2 | 0.25 |  |  | 20.8 | 20.776 | 20.776 | 20.788 | 20.776 | 20.776 | 20.776 | 20.751 | 20.772 | 20.748 | 20.748 | 20.748 | 20.735 | 20.744 | 20.744 | 20.732 | 20.744 | 20.728 | 20.716 | 20.707 | 20.728 | 0.996 | -0.0112 |  | 20.7056 | 20.6817 | 20.6817 | 20.6936 | 20.6817 | 20.6817 | 20.6817 | 20.6568 | 20.6777 | 20.6538 | 20.6538 | 20.6538 | 20.6409 | 20.6498 | 20.6498 | 20.6379 | 20.6498 | 20.6339 | 20.6219 | 20.613 | 20.6339
19 | Vertical 19 | 20.6045 | 0.023998 | 20.5678 | 20.6481 | 2.19 | 1.4 | 0.25 |  |  | 20.727 | 20.715 | 20.702 | 20.727 | 20.702 | 20.715 | 20.69 | 20.666 | 20.686 | 20.686 | 20.686 | 20.686 | 20.662 | 20.671 | 20.671 | 20.671 | 20.658 | 20.667 | 20.655 | 20.646 | 20.655 | 0.9919 | 0.089 |  | 20.6481 | 20.6362 | 20.6233 | 20.6481 | 20.6233 | 20.6362 | 20.6114 | 20.5876 | 20.6074 | 20.6074 | 20.6074 | 20.6074 | 20.5836 | 20.5926 | 20.5926 | 20.5926 | 20.5797 | 20.5886 | 20.5767 | 20.5678 | 20.5767
20 | Vertical 20 | 20.6377 | 0.024428 | 20.6059 | 20.6773 | 2.19 | 1.6 | 0.25 |  |  | 20.776 | 20.739 | 20.739 | 20.776 | 20.776 | 20.763 | 20.739 | 20.715 | 20.76 | 20.735 | 20.723 | 20.723 | 20.711 | 20.756 | 20.756 | 20.72 | 20.707 | 20.716 | 20.704 | 20.72 | 20.704 | 0.9916 | 0.0758 |  | 20.6773 | 20.6406 | 20.6406 | 20.6773 | 20.6773 | 20.6644 | 20.6406 | 20.6168 | 20.6614 | 20.6366 | 20.6247 | 20.6247 | 20.6128 | 20.6574 | 20.6574 | 20.6218 | 20.6089 | 20.6178 | 20.6059 | 20.6218 | 20.6059
21 | Vertical 21 | 20.5159 | 0.03211 | 20.4552 | 20.5751 | 2.19 | 1.8 | 0.25 |  |  | 20.443 | 20.431 | 20.431 | 20.464 | 20.443 | 20.431 | 20.403 | 20.379 | 20.412 | 20.412 | 20.375 | 20.363 | 20.396 | 20.432 | 20.432 | 20.396 | 20.371 | 20.343 | 20.38 | 20.389 | 20.364 | 0.9907 | 0.3014 |  | 20.5543 | 20.5424 | 20.5424 | 20.5751 | 20.5543 | 20.5424 | 20.5147 | 20.4909 | 20.5236 | 20.5236 | 20.4869 | 20.475 | 20.5077 | 20.5434 | 20.5434 | 20.5077 | 20.4829 | 20.4552 | 20.4919 | 20.5008 | 20.476
22 | Vertical 22 | 20.5206 | 0.026304 | 20.4728 | 20.5597 | 2.19 | 2 | 0.25 |  |  | 20.517 | 20.505 | 20.517 | 20.525 | 20.517 | 20.517 | 20.489 | 20.476 | 20.485 | 20.497 | 20.473 | 20.448 | 20.469 | 20.506 | 20.506 | 20.469 | 20.469 | 20.453 | 20.453 | 20.474 | 20.438 | 0.9991 | 0.0532 |  | 20.5517 | 20.5397 | 20.5517 | 20.5597 | 20.5517 | 20.5517 | 20.5238 | 20.5108 | 20.5198 | 20.5318 | 20.5078 | 20.4828 | 20.5038 | 20.5407 | 20.5407 | 20.5038 | 20.5038 | 20.4878 | 20.4878 | 20.5088 | 20.4728
23 | Vertical 23 | 20.5239 | 0.027203 | 20.47 | 20.5694 | 2.19 | 2.2 | 0.25 |  |  | 20.505 | 20.492 | 20.492 | 20.513 | 20.505 | 20.492 | 20.476 | 20.476 | 20.461 | 20.461 | 20.436 | 20.424 | 20.445 | 20.481 | 20.481 | 20.457 | 20.445 | 20.453 | 20.453 | 20.45 | 20.413 | 0.994 | 0.1795 |  | 20.5615 | 20.5485 | 20.5485 | 20.5694 | 20.5615 | 20.5485 | 20.5326 | 20.5326 | 20.5177 | 20.5177 | 20.4929 | 20.481 | 20.5018 | 20.5376 | 20.5376 | 20.5138 | 20.5018 | 20.5098 | 20.5098 | 20.5068 | 20.47
24 | Vertical 24 | 20.5199 | 0.029352 | 20.4616 | 20.5655 | 2.19 | 2.4 | 0.25 |  |  | 20.517 | 20.505 | 20.505 | 20.513 | 20.517 | 20.505 | 20.476 | 20.476 | 20.461 | 20.473 | 20.436 | 20.436 | 20.457 | 20.469 | 20.469 | 20.457 | 20.445 | 20.453 | 20.453 | 20.462 | 20.413 | 0.9999 | 0.0506 |  | 20.5655 | 20.5535 | 20.5535 | 20.5615 | 20.5655 | 20.5535 | 20.5246 | 20.5246 | 20.5096 | 20.5216 | 20.4846 | 20.4846 | 20.5056 | 20.5176 | 20.5176 | 20.5056 | 20.4936 | 20.5016 | 20.5016 | 20.5106 | 20.4616
25 | Air 0.1 | 19.1689 | 0.085832 | 19.006 | 19.3534 | 1.22 | 0.1 | 1.1 |  |  | 19.079 | 19.042 | 18.993 | 19.014 | 19.116 | 19.079 | 18.977 | 18.977 | 18.974 | 19.059 | 18.928 | 19.035 | 19.129 | 18.887 | 18.961 | 19.08 | 19.092 | 19.187 | 19.236 | 19.146 | 19.073 | 0.9952 | 0.2097 |  | 19.1971 | 19.1603 | 19.1115 | 19.1324 | 19.2339 | 19.1971 | 19.0956 | 19.0956 | 19.0926 | 19.1772 | 19.0468 | 19.1533 | 19.2469 | 19.006 | 19.0797 | 19.1981 | 19.2101 | 19.3046 | 19.3534 | 19.2638 | 19.1911
26 | Air 0.6 | 20.0422 | 0.041792 | 19.9641 | 20.0963 | 1.22 | 0.6 | 1.1 |  |  | 20.03 | 20.018 | 20.018 | 19.99 | 20.03 | 19.981 | 19.953 | 20.014 | 19.95 | 19.974 | 19.925 | 20.011 | 20.007 | 19.922 | 19.897 | 19.946 | 19.897 | 19.955 | 20.016 | 19.976 | 19.976 | 0.994 | 0.1865 |  | 20.0963 | 20.0844 | 20.0844 | 20.0566 | 20.0963 | 20.0476 | 20.0198 | 20.0804 | 20.0168 | 20.0407 | 19.9919 | 20.0774 | 20.0735 | 19.989 | 19.9641 | 20.0128 | 19.9641 | 20.0218 | 20.0824 | 20.0426 | 20.0426
27 | Air 1.1 | 20.5321 | 0.033823 | 20.4535 | 20.586 | 1.22 | 1.1 | 1.1 |  |  | 20.517 | 20.468 | 20.48 | 20.489 | 20.529 | 20.517 | 20.501 | 20.501 | 20.51 | 20.497 | 20.485 | 20.485 | 20.457 | 20.396 | 20.42 | 20.457 | 20.445 | 20.453 | 20.441 | 20.45 | 20.474 | 0.9962 | 0.135 |  | 20.574 | 20.5252 | 20.5372 | 20.5461 | 20.586 | 20.574 | 20.5581 | 20.5581 | 20.5671 | 20.5541 | 20.5422 | 20.5422 | 20.5143 | 20.4535 | 20.4774 | 20.5143 | 20.5023 | 20.5103 | 20.4983 | 20.5073 | 20.5312
28 | Air 1.5 | 20.6046 | 0.02637 | 20.5669 | 20.6503 | 1.22 | 1.5 | 1.1 |  |  | 20.566 | 20.529 | 20.554 | 20.574 | 20.566 | 20.578 | 20.538 | 20.525 | 20.534 | 20.534 | 20.51 | 20.51 | 20.518 | 20.555 | 20.555 | 20.506 | 20.494 | 20.502 | 20.502 | 20.523 | 20.499 | 0.9935 | 0.2061 |  | 20.6384 | 20.6017 | 20.6265 | 20.6464 | 20.6384 | 20.6503 | 20.6106 | 20.5977 | 20.6066 | 20.6066 | 20.5828 | 20.5828 | 20.5907 | 20.6275 | 20.6275 | 20.5788 | 20.5669 | 20.5748 | 20.5748 | 20.5957 | 20.5719
29 | Cieling | 20.5828 | 0.034829 | 20.5114 | 20.6386 | 0 | 2.46 | 0.6 |  |  | 20.602 | 20.59 | 20.566 | 20.587 | 20.59 | 20.578 | 20.562 | 20.562 | 20.534 | 20.559 | 20.534 | 20.546 | 20.518 | 20.555 | 20.555 | 20.506 | 20.53 | 20.515 | 20.515 | 20.486 | 20.474 | 0.9933 | 0.1746 |  | 20.6386 | 20.6266 | 20.6028 | 20.6237 | 20.6266 | 20.6147 | 20.5988 | 20.5988 | 20.571 | 20.5959 | 20.571 | 20.5829 | 20.5551 | 20.5919 | 20.5919 | 20.5432 | 20.567 | 20.5521 | 20.5521 | 20.5233 | 20.5114
30 | Floor | 20.7006 | 0.016879 | 20.6738 | 20.7333 | 1.85 | 0 | 0.6 |  |  | 20.651 | 20.664 | 20.651 | 20.66 | 20.676 | 20.676 | 20.66 | 20.685 | 20.656 | 20.669 | 20.669 | 20.644 | 20.653 | 20.641 | 20.641 | 20.628 | 20.641 | 20.625 | 20.637 | 20.633 | 20.633 | 0.9921 | 0.2117 |  | 20.6996 | 20.7125 | 20.6996 | 20.7085 | 20.7244 | 20.7244 | 20.7085 | 20.7333 | 20.7045 | 20.7174 | 20.7174 | 20.6926 | 20.7015 | 20.6896 | 20.6896 | 20.6767 | 20.6896 | 20.6738 | 20.6857 | 20.6817 | 20.6817
31 | Floor | 24.2355 | 0.016252 | 24.2048 | 24.2668 | 0.59 | 0 | 0.6 |  |  | 24.191 | 24.188 | 24.191 | 24.179 | 24.179 | 24.176 | 24.179 | 24.2 | 24.172 | 24.196 | 24.172 | 24.169 | 24.208 | 24.169 | 24.181 | 24.181 | 24.157 | 24.145 | 24.153 | 24.165 | 24.15 | 0.9847 | 0.4292 |  | 24.2501 | 24.2471 | 24.2501 | 24.2383 | 24.2383 | 24.2353 | 24.2383 | 24.2589 | 24.2314 | 24.255 | 24.2314 | 24.2284 | 24.2668 | 24.2284 | 24.2402 | 24.2402 | 24.2166 | 24.2048 | 24.2127 | 24.2245 | 24.2097
32 | Floor | 19.7247 | 0.033254 | 19.6588 | 19.7762 | 0 | 0 | 0.6 |  |  | 19.663 | 19.672 | 19.639 | 19.7 | 19.688 | 19.672 | 19.7 | 19.709 | 19.68 | 19.693 | 19.656 | 19.603 | 19.644 | 19.628 | 19.616 | 19.591 | 19.628 | 19.628 | 19.649 | 19.661 | 19.682 | 0.9948 | 0.1697 |  | 19.7305 | 19.7394 | 19.7066 | 19.7673 | 19.7553 | 19.7394 | 19.7673 | 19.7762 | 19.7474 | 19.7603 | 19.7235 | 19.6708 | 19.7116 | 19.6956 | 19.6837 | 19.6588 | 19.6956 | 19.6956 | 19.7165 | 19.7285 | 19.7494
33 | Mid cieling | 20.7042 | 0.020775 | 20.6726 | 20.7274 | 1.22 | 2.46 | 0.6 |  |  | 20.664 | 20.66 | 20.664 | 20.664 | 20.664 | 20.66 | 20.664 | 20.66 | 20.644 | 20.644 | 20.644 | 20.628 | 20.644 | 20.641 | 20.616 | 20.616 | 20.628 | 20.616 | 20.612 | 20.612 | 20.609 | 0.9972 | 0.1213 |  | 20.7274 | 20.7235 | 20.7274 | 20.7274 | 20.7274 | 20.7235 | 20.7274 | 20.7235 | 20.7075 | 20.7075 | 20.7075 | 20.6915 | 20.7075 | 20.7045 | 20.6796 | 20.6796 | 20.6915 | 20.6796 | 20.6756 | 20.6756 | 20.6726
34 | Window wall | 20.8997 | 0.015108 | 20.8738 | 20.9206 | 0.59 | 1.23 | 1.2 |  |  | 20.844 | 20.841 | 20.832 | 20.844 | 20.844 | 20.828 | 20.844 | 20.828 | 20.825 | 20.825 | 20.825 | 20.821 | 20.825 | 20.821 | 20.809 | 20.809 | 20.809 | 20.797 | 20.805 | 20.805 | 20.802 | 0.9966 | 0.1475 |  | 20.9206 | 20.9176 | 20.9087 | 20.9206 | 20.9206 | 20.9047 | 20.9206 | 20.9047 | 20.9017 | 20.9017 | 20.9017 | 20.8977 | 20.9017 | 20.8977 | 20.8857 | 20.8857 | 20.8857 | 20.8738 | 20.8818 | 20.8818 | 20.8788
35 | Window wall | 20.8502 | 0.017125 | 20.8213 | 20.8751 | 1.85 | 1.23 | 1.2 |  |  | 20.795 | 20.792 | 20.783 | 20.795 | 20.783 | 20.779 | 20.783 | 20.779 | 20.764 | 20.776 | 20.776 | 20.76 | 20.776 | 20.772 | 20.76 | 20.748 | 20.772 | 20.748 | 20.744 | 20.744 | 20.741 | 0.9957 | 0.1695 |  | 20.8751 | 20.8721 | 20.8631 | 20.8751 | 20.8631 | 20.8592 | 20.8631 | 20.8592 | 20.8442 | 20.8562 | 20.8562 | 20.8402 | 20.8562 | 20.8522 | 20.8402 | 20.8283 | 20.8522 | 20.8283 | 20.8243 | 20.8243 | 20.8213
36 | Door wall | 20.2677 | 0.023067 | 20.2308 | 20.3062 | 1.85 | 1.23 | 0 |  |  | 20.162 | 20.158 | 20.162 | 20.174 | 20.162 | 20.146 | 20.162 | 20.146 | 20.13 | 20.142 | 20.142 | 20.127 | 20.142 | 20.127 | 20.114 | 20.114 | 20.114 | 20.105 | 20.111 | 20.101 | 20.098 | 0.9912 | 0.3097 |  | 20.2943 | 20.2903 | 20.2943 | 20.3062 | 20.2943 | 20.2784 | 20.2943 | 20.2784 | 20.2626 | 20.2745 | 20.2745 | 20.2596 | 20.2745 | 20.2596 | 20.2467 | 20.2467 | 20.2467 | 20.2378 | 20.2437 | 20.2338 | 20.2308
37 | Door wall | 20.3647 | 0.024897 | 20.3238 | 20.4064 | 0.59 | 1.23 | 0 |  |  | 20.223 | 20.22 | 20.211 | 20.235 | 20.223 | 20.22 | 20.211 | 20.207 | 20.204 | 20.191 | 20.191 | 20.188 | 20.191 | 20.188 | 20.163 | 20.176 | 20.176 | 20.151 | 20.16 | 20.16 | 20.156 | 0.9828 | 0.5194 |  | 20.3946 | 20.3916 | 20.3828 | 20.4064 | 20.3946 | 20.3916 | 20.3828 | 20.3788 | 20.3759 | 20.3631 | 20.3631 | 20.3602 | 20.3631 | 20.3602 | 20.3356 | 20.3484 | 20.3484 | 20.3238 | 20.3326 | 20.3326 | 20.3287
38 | Upper outlet | 20.6326 | 0.042627 | 20.5515 | 20.7345 | 2.44 | 1.84 | 0.6 |  |  | 20.578 | 20.513 | 20.529 | 20.541 | 20.541 | 20.587 | 20.505 | 20.501 | 20.485 | 20.51 | 20.497 | 20.494 | 20.497 | 20.616 | 20.53 | 20.432 | 20.506 | 20.481 | 20.515 | 20.466 | 20.462 | 0.9946 | 0.2298 |  | 20.6967 | 20.632 | 20.6479 | 20.6599 | 20.6599 | 20.7056 | 20.6241 | 20.6201 | 20.6042 | 20.629 | 20.6161 | 20.6131 | 20.6161 | 20.7345 | 20.6489 | 20.5515 | 20.6251 | 20.6002 | 20.634 | 20.5853 | 20.5813
39 | Lower outlet | 20.2043 | 0.12118 | 19.9945 | 20.4407 | 2.44 | 0.63 | 0.6 |  |  | 20.309 | 20.134 | 20.15 | 20.186 | 20.104 | 19.929 | 20.125 | 20.088 | 20.072 | 20.084 | 20.109 | 19.922 | 19.999 | 20.032 | 19.86 | 20.068 | 20.081 | 19.873 | 20.233 | 19.906 | 20.229 | 0.9939 | 0.2556 |  | 20.4407 | 20.2668 | 20.2827 | 20.3185 | 20.237 | 20.063 | 20.2578 | 20.2211 | 20.2052 | 20.2171 | 20.2419 | 20.0561 | 20.1326 | 20.1654 | 19.9945 | 20.2012 | 20.2141 | 20.0074 | 20.3652 | 20.0402 | 20.3612
40 | Back wall | 20.8125 | 0.022644 | 20.7792 | 20.8481 | 2.44 | 1.23 | 0.6 |  |  | 20.734 | 20.743 | 20.722 | 20.734 | 20.734 | 20.73 | 20.734 | 20.73 | 20.715 | 20.702 | 20.702 | 20.699 | 20.702 | 20.699 | 20.687 | 20.687 | 20.687 | 20.677 | 20.683 | 20.674 | 20.679 | 0.9974 | 0.159 |  | 20.8391 | 20.8481 | 20.8271 | 20.8391 | 20.8391 | 20.8351 | 20.8391 | 20.8351 | 20.8201 | 20.8072 | 20.8072 | 20.8042 | 20.8072 | 20.8042 | 20.7922 | 20.7922 | 20.7922 | 20.7822 | 20.7882 | 20.7792 | 20.7842
| Air velocities: |  | Dantec Dynamics Indoor Flow System with 5 54T21 Omnidirectional Transducers.
| Position |  | Air velocities (m/s) |  |  |  | Coordinates |  |  |  | 155.9 | 150.9 | 150.8 | 155.7 | 152.6 | 150.1 | 151.9 | 151.1 | 154.6 | 155.2 | 155.4 | 155.5 | 155.5 | 158.7 | 156.5 | 154.7 | 153.2 | 152.7 | 153.9 | 153.6 | 155.2 |  | L. Foot |  | 153.9857 | 2.2064 | 150.1 | 158.7
|  | va [m/s] | STD [m/s] | Tu % |  | x | y | z |  |  | 160.4 | 158.2 | 158.6 | 160.4 | 159.4 | 156.7 | 158 | 159.6 | 160.7 | 162.9 | 161.5 | 161.9 | 161.4 | 163 | 162.9 | 161.4 | 158.8 | 159.2 | 159 | 158.9 | 159.1 |  | R. Foot |  | 160.0952 | 1.7597 | 156.7 | 163
1 | Air vel. 1 | 0.292 | 0.017 | 5.93 |  | 0.19 | 1.3 | 0 |  |  | 144.5 | 144.3 | 144.9 | 145.7 | 145.1 | 144.5 | 144.2 | 145.4 | 144.8 | 145.7 | 146.3 | 145.8 | 145.9 | 145.4 | 145 | 145.2 | 145.5 | 145.3 | 144.9 | 145.3 | 145.7 |  | L. Low leg |  | 145.2095 | 0.55579 | 144.2 | 146.3
2 | Air vel. 2 | 0.269 | 0.014 | 5.195 |  | 0.19 | 1.1 | 0 |  |  | 146.4 | 144.7 | 144.6 | 146.5 | 145.6 | 144.4 | 144.8 | 145.5 | 146.1 | 146.4 | 146.5 | 146.5 | 146.5 | 146.7 | 147.3 | 146.4 | 146.8 | 145.2 | 145.5 | 147 | 147.3 |  | R. Low leg |  | 146.0333 | 0.89238 | 144.4 | 147.3
3 | Air vel. 3 | 0.254 | 0.01 | 3.815 |  | 0.19 | 0.875 | 0 |  |  | 101.5 | 100.9 | 101.2 | 101.9 | 101.8 | 101.6 | 102.4 | 101.8 | 102.3 | 102.1 | 102.2 | 102.4 | 102.3 | 103.4 | 102 | 102 | 101.7 | 101.9 | 102.4 | 102 | 101.7 |  | L. Thigh |  | 101.9762 | 0.50981 | 100.9 | 103.4
4 | Air vel. 4 | 0.243 | 0.009 | 3.551 |  | 0.19 | 0.55 | 0 |  |  | 105.6 | 105 | 105.3 | 105.5 | 106 | 105 | 106.5 | 106.1 | 106 | 106.4 | 107.6 | 107.3 | 106.3 | 107.8 | 106.6 | 106 | 106.2 | 106.3 | 107.1 | 105.2 | 106.2 |  | R. Thigh |  | 106.1905 | 0.79114 | 105 | 107.8
5 | Air vel. 5 | 0.278 | 0.036 | 12.962 |  | 0.19 | 0.275 | 0 |  |  | 115.1 | 114.7 | 114.5 | 115.3 | 114.9 | 115.2 | 114.1 | 115.1 | 115.3 | 114.5 | 113.8 | 115 | 114.8 | 113.5 | 115.1 | 115.4 | 114.7 | 114.7 | 115 | 115.4 | 115.5 |  | Pelvis |  | 114.8381 | 0.52866 | 113.5 | 115.5
6 | Air vel. 6 | 0.186 | 0.077 | 41.344 |  | 2.19 | 1.3 | 0 |  |  | 120.6 | 120.7 | 119.9 | 121 | 120.9 | 120.2 | 120.4 | 120.2 | 121 | 121 | 121 | 121.4 | 120.9 | 121 | 121.3 | 121.5 | 121.5 | 120.9 | 121.8 | 122 | 121.2 |  | Head |  | 120.9714 | 0.52644 | 119.9 | 122
7 | Air vel. 7 | 0.228 | 0.057 | 24.867 |  | 2.19 | 1.1 | 0 |  |  | 72.7 | 72.5 | 72 | 72.4 | 72.6 | 72.4 | 72.3 | 72.2 | 72.4 | 72.4 | 72.4 | 72.3 | 72.4 | 72.2 | 72.6 | 72.9 | 72.5 | 72.3 | 72.4 | 72.7 | 72.2 |  | Top of head |  | 72.419 | 0.20401 | 72 | 72.9
8 | Air vel. 8 | 0.72 | 0.053 | 7.357 |  | 2.19 | 0.875 | 0 |  |  | 163.4 | 162.6 | 163.6 | 163.5 | 164.8 | 163.4 | 164.3 | 164.4 | 164.1 | 164.4 | 164.1 | 164.8 | 165.7 | 165.9 | 165.2 | 163.9 | 164.2 | 162.9 | 164 | 164 | 162.2 |  | L. Hand |  | 164.0667 | 0.92592 | 162.2 | 165.9
9 | Air vel. 9 | 0.982 | 0.043 | 4.383 |  | 2.19 | 0.55 | 0 |  |  | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.6 | 187.7 | 187.7 | 187.7 | 187.7 | 187.6 | 187.7 | 187.7 | 187.6 | 187.6 | 187.7 | 187.7 | 187.6 | 187.7 |  | R. Hand |  | 187.6429 | 0.050709 | 187.6 | 187.7
10 | Air vel. 10 | 0.469 | 0.032 | 6.849 |  | 2.19 | 0.275 | 0 |  |  | 152.5 | 150 | 150.3 | 149.9 | 152.9 | 149.7 | 152 | 151.7 | 151.7 | 152.9 | 151.9 | 154.3 | 153.7 | 154.8 | 153.8 | 152.1 | 151.2 | 150.6 | 151.4 | 151.4 | 150.4 |  | L. Forearm |  | 151.8667 | 1.4735 | 149.7 | 154.8
[11 empty] | 133.6 | 136.6 | 136.7 | 137.4 | 136.3 | 136.7 | 137.9 | 137.2 | 136.5 | 136.6 | 136.9 | 136.3 | 137.1 | 137.3 | 135.7 | 136.3 | 137.5 | 136.5 | 138.4 | 134.6 | 135.8 |  | R. Forearm |  | 136.5667 | 1.0561 | 133.6 | 138.4
[11 empty] | 123.1 | 123.3 | 122.6 | 123.6 | 123.4 | 123.3 | 124.2 | 123.5 | 123.8 | 124.3 | 122.6 | 123.9 | 124.2 | 123.2 | 124 | 124.4 | 123.8 | 123.4 | 123.2 | 122.9 | 123.1 |  | L. Upper arm |  | 123.5143 | 0.52942 | 122.6 | 124.4
[11 empty] | 130.7 | 131.3 | 131.1 | 131.5 | 132.1 | 131.3 | 131.6 | 132.2 | 131.4 | 131.3 | 130.5 | 131.9 | 132.5 | 130.8 | 131.8 | 131.9 | 131.4 | 131.2 | 131.2 | 131.7 | 131.2 |  | R. Upper arm |  | 131.4571 | 0.49857 | 130.5 | 132.5
[11 empty] | 118 | 118.2 | 118.3 | 118.3 | 118.9 | 118.3 | 118.5 | 119 | 118.6 | 118.3 | 118.4 | 119.3 | 119.2 | 118.6 | 118.5 | 118.6 | 118.8 | 118.8 | 118.7 | 119.1 | 118.8 |  | Chest |  | 118.6286 | 0.34662 | 118 | 119.3
[11 empty] | 112.6 | 111.9 | 111.9 | 112.1 | 112.4 | 112.8 | 112.7 | 112.7 | 112 | 112.3 | 110.5 | 111 | 113.1 | 111.1 | 112.1 | 113 | 111.9 | 111.5 | 110.9 | 111.9 | 110.4 |  | Back |  | 111.9429 | 0.79093 | 110.4 | 113.1
[11 empty] | 123.8 | 123.3 | 123.3 | 124 | 124 | 123.4 | 123.9 | 124 | 124.1 | 124.2 | 124 | 124.5 | 124.6 | 124.5 | 124.4 | 124.3 | 124 | 123.8 | 124.1 | 124 | 123.9 |  | All |  | 124.0048 | 0.36121 | 123.3 | 124.6

## HL6@va0.27ta20
Manikin heat loss in windtunnel
| Nom. Inlet velocity |  | 0.2 | m/s | Nom. Air temperature |  | 20 | ºC
| Mean Inlet velocity |  | 0.2672 | m/s | Mean Air temp. |  | 20.3034 | ºC
[10 empty] | 1 |  | 2 | [15 empty] | 2
| Std. dev. Inlet vel. |  | 0.0172 | m/s | Std. dev. Air temp. |  | 0.044068 | ºC
1
| Mean Inlet Turb. intens. |  | 6.2906 | % | Mean Wall temp. |  | 20.9293 | ºC
| Relative Humidity |  | 35 | % | Air Pressure |  | 1027.15 | mbar | 4 |  |  | 3 | [12 empty] | 6 | [6 empty] | 5
| Thermal manikin: |  | Comfortina, No clothing, Software version 3.0.30. | [6 empty] | 6 | [17 empty] | 3
| Body Segments |  | Heat loss (W/m2) | [30 empty] | H L (W/m2) | Zones | No
|  | Q [W/m2] | STD [W/m2] | Min | Max | [7 empty] | 8 |  |  |  | 10 | [7 empty] | 10 | [6 empty] | 11 |  | 124.0762 | Total | 18
1 | L. Foot | 155.3619 | 2.6943 | 150 | 159.5 | [28 empty] | 72.5 | Scalp | 9 | 1
2 | R. Foot | 160.3857 | 2.1541 | 156 | 165.8 |  |  |  |  | 17 | [23 empty] | 120.9381 | Face | 8 | 2
3 | L. Low leg | 145.1524 | 0.50756 | 144.1 | 146 | [28 empty] | 118.5143 | Chest | 16 | 3
4 | R. Low leg | 146.5524 | 1.0708 | 144.7 | 148.3 | [5 empty] | 18 |  |  |  |  | 12 | [9 empty] | 12 |  | 18 |  | 11 |  |  |  | 111.7143 | Up. back | 17 | 4
5 | L. Thigh | 101.7905 | 0.69131 | 99.9 | 103.1 | [28 empty] | 123.681 | L U arm | 14 | 5
6 | R. Thigh | 106.4048 | 0.65611 | 104.8 | 107.5 | [28 empty] | 131.4048 | R U arm | 15 | 6
7 | Pelvis | 114.8286 | 0.55601 | 113.7 | 115.7 | [28 empty] | 153.1095 | L L arm | 12 | 7
8 | Head | 120.9381 | 0.35139 | 120.4 | 121.6 | [28 empty] | 135.5619 | R L arm | 13 | 8
9 | Top of head | 72.5 | 0.34205 | 72.1 | 73.2 | [14 empty] | 14 | [5 empty] | 14 |  |  |  | 13 |  |  |  | 164.2524 | L hand | 10 | 9
10 | L. Hand | 164.2524 | 0.7737 | 162.9 | 165.5 | [28 empty] | 187.6476 | R hand | 11 | 10
11 | R. Hand | 187.6476 | 0.051177 | 187.6 | 187.7 | [28 empty] | 101.7905 | L thigh | 5 | 11
12 | L. Forearm | 153.1095 | 1.1049 | 149.7 | 154.7 |  |  |  | y | [19 empty] | y |  |  |  |  | 106.4048 | R thigh | 6 | 12
13 | R. Forearm | 135.5619 | 1.1578 | 132.8 | 137.3 | [14 empty] | 16 | [5 empty] | 16 |  |  |  | 15 |  |  |  | 145.1524 | L calf | 3 | 13
14 | L. Upper arm | 123.681 | 0.48951 | 123 | 125 | [28 empty] | 146.5524 | R calf | 4 | 14
15 | R. Upper arm | 131.4048 | 0.66444 | 130.3 | 132.6 |  |  |  | z |  |  | x | [13 empty] | z |  |  | x |  |  |  |  | 155.3619 | L foot | 1 | 15
16 | Chest | 118.5143 | 0.44078 | 117.9 | 119.5 | [28 empty] | 160.3857 | R foot | 2 | 16
17 | Back | 111.7143 | 0.87252 | 110.3 | 113.4 | [6 empty] | Corresponding zones on MANIKIN2 and 3 | [21 empty] | 111.7143 | Lo. back | 17 | 17
18 | All | 124.0762 | 0.34915 | 123.3 | 124.8 | [28 empty] | 114.8286 | Seat | 7 | 18
| Temperatures: |  | Fluke Helios Plus 2287A with 40 Thermocouple Channels.
| Position |  | Temperatures (ºC) |  |  |  | Coordinates |  |  |  | 1670-1690
|  | ta [ºC] | STD [ºC] | Min | Max | x | y | z | [23 empty] | a | b | T=ax+b
1 | Vertical 1 | 19.567 | 0.035513 | 19.5126 | 19.6229 | -1.08 | 0.2 | 0.6 |  |  | 19.589 | 19.494 | 19.543 | 19.568 | 19.58 | 19.576 | 19.519 | 19.589 | 19.564 | 19.527 | 19.527 | 19.491 | 19.478 | 19.568 | 19.536 | 19.503 | 19.499 | 19.524 | 19.491 | 19.499 | 19.524 | 0.9933 | 0.1651 |  | 19.6229 | 19.5285 | 19.5772 | 19.602 | 19.6139 | 19.6099 | 19.5533 | 19.6229 | 19.598 | 19.5613 | 19.5613 | 19.5255 | 19.5126 | 19.602 | 19.5702 | 19.5374 | 19.5335 | 19.5583 | 19.5255 | 19.5335 | 19.5583
2 | Vertical 2 | 19.8257 | 0.045416 | 19.7533 | 19.9212 | -1.08 | 0.4 | 0.6 |  |  | 19.856 | 19.785 | 19.785 | 19.809 | 19.809 | 19.879 | 19.846 | 19.904 | 19.842 | 19.891 | 19.818 | 19.781 | 19.781 | 19.809 | 19.766 | 19.781 | 19.766 | 19.778 | 19.735 | 19.766 | 19.778 | 0.9932 | 0.1525 |  | 19.8735 | 19.803 | 19.803 | 19.8268 | 19.8268 | 19.8963 | 19.8635 | 19.9212 | 19.8596 | 19.9082 | 19.8357 | 19.799 | 19.799 | 19.8268 | 19.7841 | 19.799 | 19.7841 | 19.796 | 19.7533 | 19.7841 | 19.796
3 | Vertical 3 | 20.0425 | 0.069101 | 19.9175 | 20.1851 | -1.08 | 0.6 | 0.6 |  |  | 20.113 | 20.005 | 20.005 | 20.017 | 20.017 | 20.124 | 20.103 | 20.173 | 20.197 | 20.124 | 20.1 | 20.075 | 20.063 | 20.03 | 20.01 | 20.075 | 20.01 | 19.961 | 19.928 | 19.986 | 20.01 | 0.9951 | 0.0871 |  | 20.1015 | 19.9941 | 19.9941 | 20.006 | 20.006 | 20.1125 | 20.0916 | 20.1613 | 20.1851 | 20.1125 | 20.0886 | 20.0637 | 20.0518 | 20.019 | 19.9991 | 20.0637 | 19.9991 | 19.9503 | 19.9175 | 19.9752 | 19.9991
4 | Vertical 4 | 20.2399 | 0.083101 | 20.0423 | 20.3548 | -1.08 | 0.8 | 0.6 |  |  | 20.33 | 20.238 | 20.262 | 20.32 | 20.189 | 20.283 | 20.274 | 20.353 | 20.353 | 20.197 | 20.295 | 20.295 | 20.246 | 20.226 | 20.243 | 20.271 | 20.133 | 20.108 | 20.038 | 20.12 | 20.206 | 0.9922 | 0.1606 |  | 20.332 | 20.2407 | 20.2646 | 20.3221 | 20.1921 | 20.2854 | 20.2765 | 20.3548 | 20.3548 | 20.2001 | 20.2973 | 20.2973 | 20.2487 | 20.2288 | 20.2457 | 20.2735 | 20.1366 | 20.1118 | 20.0423 | 20.1237 | 20.209
5 | Vertical 5 | 20.358 | 0.059114 | 20.2296 | 20.4419 | -1.08 | 1 | 0.6 |  |  | 20.55 | 20.492 | 20.504 | 20.528 | 20.43 | 20.513 | 20.492 | 20.513 | 20.525 | 20.488 | 20.513 | 20.488 | 20.439 | 20.467 | 20.484 | 20.476 | 20.338 | 20.399 | 20.378 | 20.362 | 20.411 | 1.0015 | -0.1389 |  | 20.4419 | 20.3838 | 20.3959 | 20.4199 | 20.3217 | 20.4049 | 20.3838 | 20.4049 | 20.4169 | 20.3798 | 20.4049 | 20.3798 | 20.3308 | 20.3588 | 20.3758 | 20.3678 | 20.2296 | 20.2907 | 20.2697 | 20.2536 | 20.3027
6 | Vertical 6 | 20.431 | 0.042027 | 20.3312 | 20.4962 | -1.08 | 1.2 | 0.6 |  |  | 20.55 | 20.516 | 20.541 | 20.565 | 20.504 | 20.537 | 20.504 | 20.513 | 20.513 | 20.537 | 20.513 | 20.5 | 20.451 | 20.516 | 20.509 | 20.513 | 20.399 | 20.472 | 20.464 | 20.423 | 20.448 | 0.994 | 0.0546 |  | 20.4813 | 20.4475 | 20.4724 | 20.4962 | 20.4356 | 20.4684 | 20.4356 | 20.4445 | 20.4445 | 20.4684 | 20.4445 | 20.4316 | 20.3829 | 20.4475 | 20.4405 | 20.4445 | 20.3312 | 20.4038 | 20.3958 | 20.3551 | 20.3799
7 | Vertical 7 | 20.5051 | 0.028413 | 20.436 | 20.5412 | -1.08 | 1.4 | 0.6 |  |  | 20.575 | 20.565 | 20.59 | 20.59 | 20.577 | 20.586 | 20.528 | 20.574 | 20.574 | 20.574 | 20.537 | 20.537 | 20.525 | 20.528 | 20.533 | 20.549 | 20.558 | 20.57 | 20.562 | 20.509 | 20.484 | 0.9922 | 0.1118 |  | 20.5263 | 20.5164 | 20.5412 | 20.5412 | 20.5283 | 20.5372 | 20.4797 | 20.5253 | 20.5253 | 20.5253 | 20.4886 | 20.4886 | 20.4767 | 20.4797 | 20.4846 | 20.5005 | 20.5094 | 20.5214 | 20.5134 | 20.4608 | 20.436
8 | Vertical 8 | 20.5263 | 0.027999 | 20.472 | 20.5771 | -1.08 | 1.6 | 0.6 |  |  | 20.66 | 20.688 | 20.7 | 20.675 | 20.675 | 20.684 | 20.639 | 20.659 | 20.672 | 20.659 | 20.623 | 20.611 | 20.611 | 20.639 | 20.631 | 20.635 | 20.644 | 20.668 | 20.635 | 20.631 | 20.595 | 1.0008 | -0.1395 |  | 20.537 | 20.5651 | 20.5771 | 20.552 | 20.552 | 20.561 | 20.516 | 20.536 | 20.549 | 20.536 | 20.5 | 20.488 | 20.488 | 20.516 | 20.508 | 20.512 | 20.521 | 20.545 | 20.512 | 20.508 | 20.472
9 | Vertical 9 | 20.5268 | 0.026709 | 20.4761 | 20.5653 | -1.08 | 1.8 | 0.6 |  |  | 20.685 | 20.7 | 20.7 | 20.688 | 20.7 | 20.708 | 20.675 | 20.672 | 20.696 | 20.672 | 20.635 | 20.623 | 20.635 | 20.688 | 20.656 | 20.672 | 20.656 | 20.68 | 20.647 | 20.656 | 20.619 | 1.0022 | -0.1883 |  | 20.5422 | 20.5572 | 20.5572 | 20.5452 | 20.5572 | 20.5653 | 20.5322 | 20.5292 | 20.5532 | 20.5292 | 20.4921 | 20.4801 | 20.4921 | 20.5452 | 20.5131 | 20.5292 | 20.5131 | 20.5372 | 20.5041 | 20.5131 | 20.4761
10 | Vertical 10 | 20.5259 | 0.032689 | 20.474 | 20.5839 | -1.08 | 2 | 0.6 |  |  | 20.709 | 20.724 | 20.724 | 20.712 | 20.724 | 20.745 | 20.712 | 20.696 | 20.708 | 20.696 | 20.659 | 20.635 | 20.647 | 20.7 | 20.68 | 20.684 | 20.656 | 20.68 | 20.647 | 20.644 | 20.644 | 0.9986 | -0.1321 |  | 20.5479 | 20.5629 | 20.5629 | 20.5509 | 20.5629 | 20.5839 | 20.5509 | 20.5349 | 20.5469 | 20.5349 | 20.498 | 20.474 | 20.486 | 20.5389 | 20.5189 | 20.5229 | 20.495 | 20.5189 | 20.486 | 20.483 | 20.483
11 | Vertical 11 | 20.5365 | 0.041503 | 20.4635 | 20.5932 | -1.08 | 2.2 | 0.6 |  |  | 20.722 | 20.749 | 20.721 | 20.728 | 20.745 | 20.736 | 20.724 | 20.721 | 20.721 | 20.696 | 20.651 | 20.659 | 20.659 | 20.712 | 20.708 | 20.68 | 20.672 | 20.672 | 20.623 | 20.619 | 20.619 | 0.9974 | -0.1019 |  | 20.5662 | 20.5932 | 20.5652 | 20.5722 | 20.5892 | 20.5802 | 20.5682 | 20.5652 | 20.5652 | 20.5403 | 20.4954 | 20.5034 | 20.5034 | 20.5562 | 20.5523 | 20.5243 | 20.5164 | 20.5164 | 20.4675 | 20.4635 | 20.4635
12 | Vertical 12 | 20.5564 | 0.037232 | 20.4752 | 20.6043 | -1.08 | 2.4 | 0.6 |  |  | 20.783 | 20.785 | 20.77 | 20.752 | 20.757 | 20.761 | 20.761 | 20.77 | 20.77 | 20.733 | 20.724 | 20.708 | 20.721 | 20.761 | 20.745 | 20.717 | 20.745 | 20.721 | 20.672 | 20.656 | 20.668 | 1.0013 | -0.2077 |  | 20.6023 | 20.6043 | 20.5893 | 20.5713 | 20.5763 | 20.5803 | 20.5803 | 20.5893 | 20.5893 | 20.5523 | 20.5432 | 20.5272 | 20.5402 | 20.5803 | 20.5643 | 20.5362 | 20.5643 | 20.5402 | 20.4912 | 20.4752 | 20.4872
13 | Vertical 13 | 19.22 | 0.065843 | 19.0631 | 19.3312 | 2.19 | 0.2 | 0.25 |  |  | 19.381 | 19.372 | 19.258 | 19.326 | 19.307 | 19.421 | 19.286 | 19.332 | 19.368 | 19.38 | 19.298 | 19.209 | 19.27 | 19.384 | 19.307 | 19.291 | 19.307 | 19.332 | 19.151 | 19.206 | 19.304 | 0.9932 | 0.0423 |  | 19.2915 | 19.2826 | 19.1693 | 19.2369 | 19.218 | 19.3312 | 19.1972 | 19.2428 | 19.2786 | 19.2905 | 19.2091 | 19.1207 | 19.1813 | 19.2945 | 19.218 | 19.2021 | 19.218 | 19.2428 | 19.0631 | 19.1177 | 19.215
14 | Vertical 14 | 20.0779 | 0.065118 | 19.9266 | 20.1739 | 2.19 | 0.4 | 0.25 |  |  | 20.235 | 20.189 | 20.161 | 20.229 | 20.161 | 20.238 | 20.201 | 20.271 | 20.234 | 20.197 | 20.226 | 20.173 | 20.149 | 20.189 | 20.185 | 20.194 | 20.173 | 20.136 | 20.063 | 20.035 | 20.022 | 0.9934 | 0.0367 |  | 20.1381 | 20.0925 | 20.0646 | 20.1322 | 20.0646 | 20.1411 | 20.1044 | 20.1739 | 20.1372 | 20.1004 | 20.1292 | 20.0766 | 20.0527 | 20.0925 | 20.0885 | 20.0974 | 20.0766 | 20.0398 | 19.9673 | 19.9395 | 19.9266
15 | Vertical 15 | 20.4224 | 0.028676 | 20.368 | 20.482 | 2.19 | 0.6 | 0.25 |  |  | 20.611 | 20.59 | 20.574 | 20.569 | 20.562 | 20.565 | 20.541 | 20.562 | 20.562 | 20.586 | 20.553 | 20.549 | 20.525 | 20.541 | 20.562 | 20.546 | 20.537 | 20.537 | 20.513 | 20.497 | 20.497 | 0.9998 | -0.1249 |  | 20.482 | 20.461 | 20.445 | 20.44 | 20.433 | 20.436 | 20.412 | 20.433 | 20.433 | 20.457 | 20.424 | 20.42 | 20.396 | 20.412 | 20.433 | 20.417 | 20.408 | 20.408 | 20.384 | 20.368 | 20.368
16 | Vertical 16 | 20.518 | 0.049086 | 20.4104 | 20.5928 | 2.19 | 0.8 | 0.25 |  |  | 20.66 | 20.614 | 20.623 | 20.63 | 20.586 | 20.602 | 20.59 | 20.623 | 20.635 | 20.598 | 20.59 | 20.611 | 20.562 | 20.59 | 20.611 | 20.607 | 20.537 | 20.513 | 20.476 | 20.484 | 20.533 | 0.9912 | 0.1146 |  | 20.5928 | 20.5472 | 20.5561 | 20.5631 | 20.5194 | 20.5353 | 20.5234 | 20.5561 | 20.568 | 20.5313 | 20.5234 | 20.5442 | 20.4957 | 20.5234 | 20.5442 | 20.5403 | 20.4709 | 20.4471 | 20.4104 | 20.4183 | 20.4669
17 | Vertical 17 | 20.5768 | 0.032546 | 20.5206 | 20.6338 | 2.19 | 1 | 0.25 |  |  | 20.709 | 20.688 | 20.684 | 20.691 | 20.672 | 20.688 | 20.663 | 20.659 | 20.672 | 20.672 | 20.639 | 20.635 | 20.611 | 20.639 | 20.659 | 20.644 | 20.623 | 20.635 | 20.598 | 20.595 | 20.607 | 0.9928 | 0.0739 |  | 20.6338 | 20.6129 | 20.609 | 20.6159 | 20.5971 | 20.6129 | 20.5881 | 20.5842 | 20.5971 | 20.5971 | 20.5643 | 20.5603 | 20.5365 | 20.5643 | 20.5842 | 20.5693 | 20.5484 | 20.5603 | 20.5236 | 20.5206 | 20.5325
18 | Vertical 18 | 20.6226 | 0.032128 | 20.5741 | 20.6668 | 2.19 | 1.2 | 0.25 |  |  | 20.758 | 20.761 | 20.757 | 20.74 | 20.745 | 20.761 | 20.736 | 20.733 | 20.733 | 20.745 | 20.7 | 20.696 | 20.684 | 20.7 | 20.708 | 20.705 | 20.684 | 20.696 | 20.672 | 20.668 | 20.668 | 0.996 | -0.0112 |  | 20.6638 | 20.6668 | 20.6628 | 20.6458 | 20.6508 | 20.6668 | 20.6419 | 20.6389 | 20.6389 | 20.6508 | 20.606 | 20.602 | 20.5901 | 20.606 | 20.614 | 20.611 | 20.5901 | 20.602 | 20.5781 | 20.5741 | 20.5741
19 | Vertical 19 | 20.5651 | 0.031103 | 20.5172 | 20.6094 | 2.19 | 1.4 | 0.25 |  |  | 20.673 | 20.675 | 20.672 | 20.679 | 20.684 | 20.688 | 20.663 | 20.647 | 20.659 | 20.672 | 20.626 | 20.611 | 20.598 | 20.614 | 20.647 | 20.631 | 20.611 | 20.647 | 20.623 | 20.595 | 20.595 | 0.9919 | 0.089 |  | 20.5945 | 20.5965 | 20.5936 | 20.6005 | 20.6055 | 20.6094 | 20.5846 | 20.5688 | 20.5807 | 20.5936 | 20.5479 | 20.5331 | 20.5202 | 20.536 | 20.5688 | 20.5529 | 20.5331 | 20.5688 | 20.545 | 20.5172 | 20.5172
20 | Vertical 20 | 20.5983 | 0.032969 | 20.5335 | 20.6505 | 2.19 | 1.6 | 0.25 |  |  | 20.746 | 20.749 | 20.721 | 20.728 | 20.721 | 20.712 | 20.7 | 20.696 | 20.721 | 20.721 | 20.675 | 20.672 | 20.647 | 20.675 | 20.721 | 20.705 | 20.684 | 20.696 | 20.659 | 20.631 | 20.644 | 0.9916 | 0.0758 |  | 20.6475 | 20.6505 | 20.6227 | 20.6297 | 20.6227 | 20.6138 | 20.6019 | 20.598 | 20.6227 | 20.6227 | 20.5771 | 20.5742 | 20.5494 | 20.5771 | 20.6227 | 20.6069 | 20.5861 | 20.598 | 20.5613 | 20.5335 | 20.5464
21 | Vertical 21 | 20.4796 | 0.022317 | 20.4245 | 20.5255 | 2.19 | 1.8 | 0.25 |  |  | 20.414 | 20.384 | 20.384 | 20.372 | 20.372 | 20.344 | 20.393 | 20.381 | 20.365 | 20.377 | 20.353 | 20.368 | 20.356 | 20.365 | 20.377 | 20.365 | 20.389 | 20.349 | 20.328 | 20.312 | 20.373 | 0.9907 | 0.3014 |  | 20.5255 | 20.4958 | 20.4958 | 20.4839 | 20.4839 | 20.4562 | 20.5047 | 20.4929 | 20.477 | 20.4889 | 20.4651 | 20.48 | 20.4681 | 20.477 | 20.4889 | 20.477 | 20.5008 | 20.4612 | 20.4403 | 20.4245 | 20.4849
22 | Vertical 22 | 20.4869 | 0.025455 | 20.4209 | 20.5288 | 2.19 | 2 | 0.25 |  |  | 20.487 | 20.494 | 20.494 | 20.482 | 20.445 | 20.43 | 20.454 | 20.466 | 20.45 | 20.463 | 20.438 | 20.43 | 20.454 | 20.45 | 20.463 | 20.463 | 20.438 | 20.435 | 20.426 | 20.386 | 20.447 | 0.9991 | 0.0532 |  | 20.5218 | 20.5288 | 20.5288 | 20.5168 | 20.4798 | 20.4648 | 20.4888 | 20.5008 | 20.4848 | 20.4978 | 20.4728 | 20.4648 | 20.4888 | 20.4848 | 20.4978 | 20.4978 | 20.4728 | 20.4698 | 20.4608 | 20.4209 | 20.4818
23 | Vertical 23 | 20.4921 | 0.023656 | 20.4303 | 20.5316 | 2.19 | 2.2 | 0.25 |  |  | 20.475 | 20.47 | 20.47 | 20.445 | 20.421 | 20.417 | 20.454 | 20.454 | 20.438 | 20.426 | 20.438 | 20.43 | 20.442 | 20.414 | 20.438 | 20.45 | 20.438 | 20.422 | 20.414 | 20.373 | 20.41 | 0.994 | 0.1795 |  | 20.5316 | 20.5267 | 20.5267 | 20.5018 | 20.478 | 20.474 | 20.5108 | 20.5108 | 20.4949 | 20.4829 | 20.4949 | 20.4869 | 20.4988 | 20.471 | 20.4949 | 20.5068 | 20.4949 | 20.479 | 20.471 | 20.4303 | 20.467
24 | Vertical 24 | 20.4942 | 0.024566 | 20.4346 | 20.5306 | 2.19 | 2.4 | 0.25 |  |  | 20.475 | 20.482 | 20.482 | 20.458 | 20.433 | 20.43 | 20.466 | 20.466 | 20.45 | 20.45 | 20.438 | 20.442 | 20.454 | 20.426 | 20.45 | 20.475 | 20.438 | 20.422 | 20.414 | 20.386 | 20.422 | 0.9999 | 0.0506 |  | 20.5236 | 20.5306 | 20.5306 | 20.5066 | 20.4816 | 20.4786 | 20.5146 | 20.5146 | 20.4986 | 20.4986 | 20.4866 | 20.4906 | 20.5026 | 20.4746 | 20.4986 | 20.5236 | 20.4866 | 20.4706 | 20.4626 | 20.4346 | 20.4706
25 | Air 0.1 | 19.2474 | 0.096077 | 19.0419 | 19.3812 | 1.22 | 0.1 | 1.1 |  |  | 19.221 | 19.264 | 19.228 | 19.191 | 19.02 | 19.065 | 19.138 | 19.2 | 19.135 | 19.171 | 19.184 | 19.138 | 19.2 | 19.196 | 19.22 | 19 | 18.951 | 18.923 | 19.025 | 19.107 | 19.143 | 0.9952 | 0.2097 |  | 19.3384 | 19.3812 | 19.3454 | 19.3086 | 19.1384 | 19.1832 | 19.2558 | 19.3175 | 19.2529 | 19.2887 | 19.3016 | 19.2558 | 19.3175 | 19.3136 | 19.3374 | 19.1185 | 19.0697 | 19.0419 | 19.1434 | 19.225 | 19.2608
26 | Air 0.6 | 20.0283 | 0.038393 | 19.9582 | 20.0953 | 1.22 | 0.6 | 1.1 |  |  | 19.989 | 19.971 | 19.983 | 20.008 | 19.959 | 19.992 | 19.955 | 20.029 | 19.988 | 19.964 | 20.013 | 19.98 | 19.98 | 19.891 | 19.903 | 19.964 | 19.927 | 19.911 | 19.952 | 19.936 | 19.899 | 0.994 | 0.1865 |  | 20.0556 | 20.0377 | 20.0496 | 20.0745 | 20.0257 | 20.0585 | 20.0218 | 20.0953 | 20.0546 | 20.0307 | 20.0794 | 20.0466 | 20.0466 | 19.9582 | 19.9701 | 20.0307 | 19.9939 | 19.978 | 20.0188 | 20.0029 | 19.9661
27 | Air 1.1 | 20.4665 | 0.040656 | 20.3698 | 20.5272 | 1.22 | 1.1 | 1.1 |  |  | 20.451 | 20.433 | 20.47 | 20.47 | 20.421 | 20.442 | 20.417 | 20.442 | 20.426 | 20.389 | 20.438 | 20.417 | 20.381 | 20.389 | 20.402 | 20.426 | 20.377 | 20.312 | 20.34 | 20.361 | 20.386 | 0.9962 | 0.135 |  | 20.5083 | 20.4904 | 20.5272 | 20.5272 | 20.4784 | 20.4993 | 20.4744 | 20.4993 | 20.4834 | 20.4465 | 20.4953 | 20.4744 | 20.4386 | 20.4465 | 20.4595 | 20.4834 | 20.4346 | 20.3698 | 20.3977 | 20.4186 | 20.4435
28 | Air 1.5 | 20.5617 | 0.025967 | 20.5083 | 20.6036 | 1.22 | 1.5 | 1.1 |  |  | 20.524 | 20.519 | 20.531 | 20.507 | 20.519 | 20.503 | 20.515 | 20.478 | 20.499 | 20.499 | 20.475 | 20.466 | 20.454 | 20.475 | 20.499 | 20.499 | 20.475 | 20.459 | 20.463 | 20.435 | 20.471 | 0.9935 | 0.2061 |  | 20.5967 | 20.5917 | 20.6036 | 20.5798 | 20.5917 | 20.5758 | 20.5878 | 20.551 | 20.5719 | 20.5719 | 20.548 | 20.5391 | 20.5271 | 20.548 | 20.5719 | 20.5719 | 20.548 | 20.5321 | 20.5361 | 20.5083 | 20.544
29 | Cieling | 20.55 | 0.029162 | 20.4965 | 20.5929 | 0 | 2.46 | 0.6 |  |  | 20.549 | 20.556 | 20.531 | 20.531 | 20.519 | 20.54 | 20.54 | 20.552 | 20.512 | 20.499 | 20.512 | 20.515 | 20.527 | 20.512 | 20.524 | 20.499 | 20.487 | 20.459 | 20.475 | 20.459 | 20.471 | 0.9933 | 0.1746 |  | 20.5859 | 20.5929 | 20.568 | 20.568 | 20.5561 | 20.577 | 20.577 | 20.5889 | 20.5492 | 20.5363 | 20.5492 | 20.5521 | 20.5641 | 20.5492 | 20.5611 | 20.5363 | 20.5243 | 20.4965 | 20.5124 | 20.4965 | 20.5084
30 | Floor | 20.7021 | 0.014365 | 20.6787 | 20.7234 | 1.85 | 0 | 0.6 |  |  | 20.668 | 20.663 | 20.675 | 20.663 | 20.675 | 20.659 | 20.671 | 20.671 | 20.643 | 20.655 | 20.668 | 20.647 | 20.647 | 20.634 | 20.643 | 20.643 | 20.634 | 20.63 | 20.643 | 20.64 | 20.652 | 0.9921 | 0.2117 |  | 20.7164 | 20.7115 | 20.7234 | 20.7115 | 20.7234 | 20.7075 | 20.7194 | 20.7194 | 20.6916 | 20.7035 | 20.7164 | 20.6956 | 20.6956 | 20.6827 | 20.6916 | 20.6916 | 20.6827 | 20.6787 | 20.6916 | 20.6886 | 20.7005
31 | Floor | 24.2946 | 0.023017 | 24.254 | 24.3308 | 0.59 | 0 | 0.6 |  |  | 24.255 | 24.229 | 24.241 | 24.253 | 24.214 | 24.249 | 24.261 | 24.261 | 24.226 | 24.246 | 24.249 | 24.249 | 24.246 | 24.258 | 24.273 | 24.234 | 24.21 | 24.198 | 24.195 | 24.195 | 24.218 | 0.9847 | 0.4292 |  | 24.3131 | 24.2875 | 24.2993 | 24.3111 | 24.2727 | 24.3072 | 24.319 | 24.319 | 24.2845 | 24.3042 | 24.3072 | 24.3072 | 24.3042 | 24.3161 | 24.3308 | 24.2924 | 24.2688 | 24.257 | 24.254 | 24.254 | 24.2767
32 | Floor | 19.7713 | 0.035999 | 19.7135 | 19.826 | 0 | 0 | 0.6 |  |  | 19.704 | 19.69 | 19.665 | 19.702 | 19.723 | 19.759 | 19.759 | 19.747 | 19.747 | 19.756 | 19.723 | 19.711 | 19.646 | 19.646 | 19.674 | 19.682 | 19.695 | 19.682 | 19.667 | 19.679 | 19.728 | 0.9948 | 0.1697 |  | 19.7712 | 19.7573 | 19.7324 | 19.7692 | 19.7901 | 19.826 | 19.826 | 19.814 | 19.814 | 19.823 | 19.7901 | 19.7782 | 19.7135 | 19.7135 | 19.7414 | 19.7494 | 19.7623 | 19.7494 | 19.7344 | 19.7464 | 19.7951
33 | Mid cieling | 20.6787 | 0.01967 | 20.6457 | 20.7135 | 1.22 | 2.46 | 0.6 |  |  | 20.643 | 20.65 | 20.641 | 20.629 | 20.613 | 20.625 | 20.638 | 20.638 | 20.613 | 20.609 | 20.613 | 20.613 | 20.609 | 20.597 | 20.625 | 20.609 | 20.597 | 20.585 | 20.594 | 20.582 | 20.594 | 0.9972 | 0.1213 |  | 20.7065 | 20.7135 | 20.7045 | 20.6925 | 20.6766 | 20.6885 | 20.7015 | 20.7015 | 20.6766 | 20.6726 | 20.6766 | 20.6766 | 20.6726 | 20.6606 | 20.6885 | 20.6726 | 20.6606 | 20.6487 | 20.6576 | 20.6457 | 20.6576
34 | Window wall | 20.8785 | 0.017103 | 20.8509 | 20.9127 | 0.59 | 1.23 | 1.2 |  |  | 20.836 | 20.822 | 20.822 | 20.822 | 20.806 | 20.818 | 20.806 | 20.818 | 20.794 | 20.802 | 20.806 | 20.806 | 20.79 | 20.79 | 20.806 | 20.79 | 20.778 | 20.778 | 20.774 | 20.786 | 20.786 | 0.9966 | 0.1475 |  | 20.9127 | 20.8987 | 20.8987 | 20.8987 | 20.8828 | 20.8947 | 20.8828 | 20.8947 | 20.8708 | 20.8788 | 20.8828 | 20.8828 | 20.8668 | 20.8668 | 20.8828 | 20.8668 | 20.8549 | 20.8549 | 20.8509 | 20.8628 | 20.8628
35 | Window wall | 20.8353 | 0.016105 | 20.8094 | 20.8671 | 1.85 | 1.23 | 1.2 |  |  | 20.787 | 20.773 | 20.773 | 20.773 | 20.769 | 20.757 | 20.757 | 20.769 | 20.745 | 20.753 | 20.757 | 20.769 | 20.753 | 20.753 | 20.757 | 20.741 | 20.729 | 20.729 | 20.737 | 20.737 | 20.737 | 0.9957 | 0.1695 |  | 20.8671 | 20.8532 | 20.8532 | 20.8532 | 20.8492 | 20.8372 | 20.8372 | 20.8492 | 20.8253 | 20.8333 | 20.8372 | 20.8492 | 20.8333 | 20.8333 | 20.8372 | 20.8213 | 20.8094 | 20.8094 | 20.8173 | 20.8173 | 20.8173
36 | Door wall | 20.2779 | 0.018887 | 20.2487 | 20.3101 | 1.85 | 1.23 | 0 |  |  | 20.178 | 20.176 | 20.164 | 20.152 | 20.16 | 20.173 | 20.148 | 20.16 | 20.136 | 20.144 | 20.148 | 20.16 | 20.132 | 20.132 | 20.148 | 20.132 | 20.132 | 20.12 | 20.116 | 20.116 | 20.129 | 0.9912 | 0.3097 |  | 20.3101 | 20.3082 | 20.2963 | 20.2844 | 20.2923 | 20.3052 | 20.2804 | 20.2923 | 20.2685 | 20.2764 | 20.2804 | 20.2923 | 20.2645 | 20.2645 | 20.2804 | 20.2645 | 20.2645 | 20.2526 | 20.2487 | 20.2487 | 20.2616
37 | Door wall | 20.3751 | 0.021306 | 20.3376 | 20.4103 | 0.59 | 1.23 | 0 |  |  | 20.239 | 20.225 | 20.225 | 20.225 | 20.222 | 20.222 | 20.222 | 20.209 | 20.197 | 20.218 | 20.209 | 20.209 | 20.193 | 20.181 | 20.209 | 20.181 | 20.193 | 20.181 | 20.165 | 20.165 | 20.178 | 0.9828 | 0.5194 |  | 20.4103 | 20.3965 | 20.3965 | 20.3965 | 20.3936 | 20.3936 | 20.3936 | 20.3808 | 20.369 | 20.3897 | 20.3808 | 20.3808 | 20.3651 | 20.3533 | 20.3808 | 20.3533 | 20.3651 | 20.3533 | 20.3376 | 20.3376 | 20.3503
38 | Upper outlet | 20.6011 | 0.042511 | 20.5177 | 20.6668 | 2.44 | 1.84 | 0.6 |  |  | 20.533 | 20.543 | 20.519 | 20.507 | 20.515 | 20.503 | 20.503 | 20.491 | 20.503 | 20.45 | 20.442 | 20.454 | 20.463 | 20.548 | 20.478 | 20.487 | 20.499 | 20.438 | 20.398 | 20.398 | 20.447 | 0.9946 | 0.2298 |  | 20.6519 | 20.6619 | 20.638 | 20.6261 | 20.634 | 20.6221 | 20.6221 | 20.6101 | 20.6221 | 20.5694 | 20.5614 | 20.5733 | 20.5823 | 20.6668 | 20.5972 | 20.6062 | 20.6181 | 20.5574 | 20.5177 | 20.5177 | 20.5664
39 | Lower outlet | 20.1701 | 0.11151 | 19.9636 | 20.39 | 2.44 | 0.63 | 0.6 |  |  | 20.022 | 19.971 | 20.213 | 20.008 | 20.258 | 20.16 | 20.016 | 20.099 | 20.099 | 19.964 | 20.099 | 19.906 | 19.829 | 19.842 | 19.98 | 20.169 | 20.05 | 19.988 | 20.116 | 19.96 | 20.022 | 0.9939 | 0.2556 |  | 20.1555 | 20.1048 | 20.3453 | 20.1416 | 20.39 | 20.2926 | 20.1495 | 20.232 | 20.232 | 20.0978 | 20.232 | 20.0402 | 19.9636 | 19.9766 | 20.1137 | 20.3016 | 20.1833 | 20.1217 | 20.2489 | 20.0938 | 20.1555
40 | Back wall | 20.7969 | 0.021727 | 20.7573 | 20.8431 | 2.44 | 1.23 | 0.6 |  |  | 20.738 | 20.712 | 20.712 | 20.712 | 20.708 | 20.72 | 20.696 | 20.708 | 20.684 | 20.692 | 20.696 | 20.696 | 20.68 | 20.68 | 20.696 | 20.68 | 20.668 | 20.668 | 20.664 | 20.652 | 20.664 | 0.9974 | 0.159 |  | 20.8431 | 20.8171 | 20.8171 | 20.8171 | 20.8132 | 20.8251 | 20.8012 | 20.8132 | 20.7892 | 20.7972 | 20.8012 | 20.8012 | 20.7852 | 20.7852 | 20.8012 | 20.7852 | 20.7733 | 20.7733 | 20.7693 | 20.7573 | 20.7693
| Air velocities: |  | Dantec Dynamics Indoor Flow System with 5 54T21 Omnidirectional Transducers.
| Position |  | Air velocities (m/s) |  |  |  | Coordinates |  |  |  | 159.5 | 157.2 | 153.6 | 150 | 155.7 | 155.6 | 150.9 | 152.8 | 158.3 | 155.4 | 158.4 | 159.1 | 159 | 154.5 | 151.7 | 154.2 | 155.3 | 154.7 | 154.6 | 154.7 | 157.4 |  | L. Foot |  | 155.3619 | 2.6943 | 150 | 159.5
|  | va [m/s] | STD [m/s] | Tu % |  | x | y | z |  |  | 162.8 | 161.2 | 159.3 | 156 | 162.3 | 160.1 | 158.3 | 157.9 | 161.2 | 161.4 | 165.8 | 161.8 | 160.5 | 159.8 | 158.2 | 160.2 | 163.1 | 161 | 158.5 | 159.3 | 159.4 |  | R. Foot |  | 160.3857 | 2.1541 | 156 | 165.8
1 | Air vel. 1 | 0.292 | 0.017 | 5.93 |  | 0.19 | 1.3 | 0 |  |  | 145.4 | 145.7 | 145.1 | 144.1 | 145.9 | 145 | 144.5 | 145.1 | 145.1 | 145.5 | 146 | 145.9 | 145.8 | 145 | 144.8 | 144.6 | 144.7 | 145.2 | 144.9 | 144.8 | 145.1 |  | L. Low leg |  | 145.1524 | 0.50756 | 144.1 | 146
2 | Air vel. 2 | 0.269 | 0.014 | 5.195 |  | 0.19 | 1.1 | 0 |  |  | 148.3 | 147.7 | 145.4 | 144.7 | 147.3 | 146.5 | 144.8 | 145.9 | 147.5 | 146.4 | 147.2 | 147.7 | 148.1 | 145.6 | 145.1 | 146 | 146.1 | 146.5 | 147 | 146.3 | 147.5 |  | R. Low leg |  | 146.5524 | 1.0708 | 144.7 | 148.3
3 | Air vel. 3 | 0.254 | 0.01 | 3.815 |  | 0.19 | 0.875 | 0 |  |  | 101.3 | 101.5 | 101.6 | 99.9 | 102.1 | 101.7 | 101.1 | 102 | 102.7 | 102.3 | 103.1 | 102.3 | 102.5 | 102.3 | 100.9 | 101.9 | 102 | 101.9 | 101.4 | 101.7 | 101.4 |  | L. Thigh |  | 101.7905 | 0.69131 | 99.9 | 103.1
4 | Air vel. 4 | 0.243 | 0.009 | 3.551 |  | 0.19 | 0.55 | 0 |  |  | 106 | 106.5 | 105.9 | 104.8 | 106.9 | 106.7 | 105.6 | 106.8 | 106.6 | 107.5 | 106.8 | 107.1 | 107.5 | 107 | 106 | 106.3 | 106 | 106.6 | 106.2 | 105.8 | 105.9 |  | R. Thigh |  | 106.4048 | 0.65611 | 104.8 | 107.5
5 | Air vel. 5 | 0.278 | 0.036 | 12.962 |  | 0.19 | 0.275 | 0 |  |  | 113.7 | 114.5 | 115 | 115.2 | 115.2 | 115.1 | 114.9 | 115.6 | 114.5 | 113.9 | 114.7 | 113.8 | 115.2 | 114.5 | 115 | 114.9 | 114.6 | 115.1 | 115.7 | 115.6 | 114.7 |  | Pelvis |  | 114.8286 | 0.55601 | 113.7 | 115.7
6 | Air vel. 6 | 0.186 | 0.077 | 41.344 |  | 2.19 | 1.3 | 0 |  |  | 120.6 | 120.4 | 120.6 | 120.8 | 120.9 | 120.6 | 120.9 | 121.1 | 120.7 | 120.4 | 121.4 | 120.8 | 121.6 | 120.7 | 121 | 121.3 | 121 | 120.8 | 121.4 | 121.4 | 121.3 |  | Head |  | 120.9381 | 0.35139 | 120.4 | 121.6
7 | Air vel. 7 | 0.228 | 0.057 | 24.867 |  | 2.19 | 1.1 | 0 |  |  | 72.2 | 72.2 | 72.4 | 72.5 | 72.5 | 72.2 | 72.6 | 72.2 | 72.1 | 72.2 | 72.2 | 72.2 | 72.4 | 72.2 | 72.8 | 72.9 | 72.9 | 72.9 | 73.1 | 73.2 | 72.6 |  | Top of head |  | 72.5 | 0.34205 | 72.1 | 73.2
8 | Air vel. 8 | 0.72 | 0.053 | 7.357 |  | 2.19 | 0.875 | 0 |  |  | 164.8 | 164.1 | 163.8 | 163.4 | 163.7 | 163.3 | 162.9 | 163.5 | 164.3 | 165 | 164.9 | 165.5 | 164.7 | 165.5 | 164.2 | 163.8 | 164.8 | 165.4 | 164 | 164.4 | 163.3 |  | L. Hand |  | 164.2524 | 0.7737 | 162.9 | 165.5
9 | Air vel. 9 | 0.982 | 0.043 | 4.383 |  | 2.19 | 0.55 | 0 |  |  | 187.6 | 187.7 | 187.6 | 187.6 | 187.6 | 187.7 | 187.6 | 187.6 | 187.6 | 187.6 | 187.7 | 187.7 | 187.7 | 187.7 | 187.7 | 187.7 | 187.7 | 187.6 | 187.6 | 187.7 | 187.6 |  | R. Hand |  | 187.6476 | 0.051177 | 187.6 | 187.7
10 | Air vel. 10 | 0.469 | 0.032 | 6.849 |  | 2.19 | 0.275 | 0 |  |  | 154.2 | 153 | 153.1 | 153.1 | 152.8 | 152.5 | 149.7 | 151.8 | 152.9 | 154.2 | 153.7 | 154.5 | 153.5 | 153.9 | 152.8 | 153.4 | 154.7 | 154 | 152 | 153 | 152.5 |  | L. Forearm |  | 153.1095 | 1.1049 | 149.7 | 154.7
[11 empty] | 132.8 | 134.1 | 135 | 134.3 | 135.3 | 135.3 | 137.3 | 137.1 | 135.4 | 136.3 | 136.1 | 136.8 | 137.2 | 137.1 | 135.6 | 135 | 134.5 | 135.4 | 135.9 | 135.5 | 134.8 |  | R. Forearm |  | 135.5619 | 1.1578 | 132.8 | 137.3
[11 empty] | 123.4 | 123.3 | 123.6 | 123.3 | 124.1 | 123 | 123.9 | 123.4 | 123.3 | 123.3 | 123.8 | 124.1 | 124.4 | 123.3 | 123.1 | 123.5 | 124.1 | 123.8 | 124.1 | 125 | 123.5 |  | L. Upper arm |  | 123.681 | 0.48951 | 123 | 125
[11 empty] | 130.7 | 130.3 | 131.1 | 131.7 | 130.9 | 130.3 | 131.6 | 132 | 130.7 | 130.4 | 131.1 | 131.4 | 131.8 | 131.7 | 131.8 | 132.4 | 131.9 | 131.6 | 132 | 132.6 | 131.5 |  | R. Upper arm |  | 131.4048 | 0.66444 | 130.3 | 132.6
[11 empty] | 118.2 | 117.9 | 118.3 | 118.3 | 118.1 | 118.1 | 118.6 | 119.2 | 118.7 | 117.9 | 118.5 | 118.4 | 119.5 | 118.5 | 118.3 | 118.2 | 118.6 | 118.5 | 118.8 | 119.4 | 118.8 |  | Chest |  | 118.5143 | 0.44078 | 117.9 | 119.5
[11 empty] | 111 | 110.3 | 112 | 113.1 | 111.8 | 110.6 | 112.2 | 111.4 | 111.1 | 111 | 111.1 | 110.9 | 111.1 | 111.4 | 111.8 | 111.8 | 112.8 | 113.2 | 112.4 | 113.4 | 111.6 |  | Back |  | 111.7143 | 0.87252 | 110.3 | 113.4
[11 empty] | 123.9 | 123.8 | 123.8 | 123.3 | 124.3 | 123.8 | 123.6 | 124.1 | 124.2 | 124 | 124.6 | 124.4 | 124.8 | 124.1 | 123.7 | 124 | 124.3 | 124.3 | 124.2 | 124.4 | 124 |  | All |  | 124.0762 | 0.34915 | 123.3 | 124.8